## 307.1(1)
TABLE 307.1(1)
MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF HAZARDOUS MATERIALS POSING A PHYSICAL HAZARDa, j, m, n, q
MATERIAL | CLASS | GROUP WHEN THE MAXIMUM ALLOWABLE QUANTITY IS EXCEEDEDq | STORAGEb |  |  | USE-CLOSED SYSTEMSb |  |  | USE-OPEN SYSTEMSb
|  |  | Solid Pounds (cubic feet) | Liquid Gallons (pounds) | Gas SCF | Solid Pounds (cubic feet) | Liquid gallons (pounds) | Gas SCF | Solid Pounds (cubic feet) | Liquid gallons (pounds)
Combustible liquid c, i, r | II IIIA IIIB | H-2 or H-3 H-2 or H-3 Not Applicable | Not Applicable | 120d, e 330d, e 13,200e, f | Not Applicable | Not Applicable | 120d 330d 13,200f | Not Applicable | Not Applicable | 30d 80d 3,300f
Combustible fiber | Loose Baleds | H-3 | (100) (1,000) | Not Applicable | Not Applicable | (100) (1,000) | Not Applicable | Not Applicable | (20) (200) | Not Applicable
Cryogenics flammable | Not Applicable | H-2 | Not Applicable | 45d | Not Applicable | Not Applicable | 45d | Not Applicable | Not Applicable | 10d
Cryogenics oxidizing | Not Applicable | H-3 | Not Applicable | 45d | Not Applicable | Not Applicable | 45d | Not Applicable | Not Applicable | 10d
Explosives | Division 1.1 Division 1.2 Division 1.3 Division 1.4 Division 1.4G Division 1.5 Division 1.6 | H-1 H-1 H-1 or H-2 H-3 H-3 H-1 H-1 | 1e, g 1e, g 5e, g 50e, g 125d, e, l 1e, g 1d, e, g | (1)e, g (1)e, g (5)e, g (50)e, g Not Applicable (1)e, g Not Applicable | Not Applicable | 0.25g 0.25g 1g 50g Not Applicable 0.25g Not Applicable | (0.25)g (0.25)g (1)g (50)g Not Applicable (0.25)g Not Applicable | Not Applicable | 0.25g 0.25g 1g Not Applicable Not Applicable 0.25g Not Applicable | (0.25)g (0.25)g (1)g Not Applicable Not Applicable (0.25)g Not Applicable
Flammable gas | Gaseous Liquefied | H-2 | Not Applicable | Not Applicable (150)d, e | 1,000d, e Not Applicable | Not Applicable | Not Applicable (150)d, e | 1,000d, e Not Applicable | Not Applicable | Not Applicable
Flammable liquids c, k | IAo IB and IC | H-2 or H-3 | Not Applicable | 30d, e 120d, e | Not Applicable | Not Applicable | 30d 120d | Not Applicable | Not Applicable | 10d 30d
Combination Flammable liquid (IAo, IB, IC) | Not Applicable | H-2 or H-3 | Not Applicable | 120d, e, h | Not Applicable | Not Applicable | 120d, h | Not Applicable | Not Applicable | 30d, h
Flammable solid | Not Applicable | H-3 | 1,000d, e 125d, e 1d, e 125d, e | Not Applicable | Not Applicable | 1,000d 125d 1d 125d | Not Applicable | Not Applicable | 1,000d 25d 1d 25d | Not Applicable
Inert gas | Gaseous Liquefied | Not Applicable | Not Applicable | Not Applicable | Not Limited | Not Applicable | Not Applicable | Not Limited | Not Applicable | Not Applicable
Cryogenic inert | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Limited | Not Applicable | Not Applicable | Not Limited | Not Applicable | Not Applicable
Organic peroxide p | Unclassified Detonable I II III IV V | H-1 H-2 H-3 H-3 Not Applicable Not Applicable | 1e, g 5d, e 50d, e 125d, e Not Limited Not Limited | (1)e, g (5)d, e (50)d, e (125)d, e Not Limited Not Limited | Not Applicable | 0.25g 1d 50d 125d Not Limited Not Limited | (0.25)g (1)d (50)d (125)d Not Limited Not Limited | Not Applicable | 0.25g 1d 10d 25d Not Limited Not Limited | (0.25)g (1)d (10)d (25)d Not Limited Not Limited
Oxidizer | 4 3k 2 1 | H-1 H-2 H-3 H-3 | 1g 10d, e 250d, e 4,000e, f | (1)e, g (10)d, e (250)d, e (4,000)e, f | Not Applicable | 0.25g 2d 250d 4,000f | (0.25)g (2)d (250)d (4,000)f | Not Applicable | 0.25g 2d 50d 1,000f | (0.25)g (2)d (50)d (1,000)f
Oxidizing gas | Gaseous Liquefied | H-3 | Not Applicable | Not Applicable (150)d, e | 1,500d, e Not Applicable | Not Applicable | Not Applicable (150)d, e | 1,500d, e Not Applicable | Not Applicable | Not Applicable
Pyrophoric material p detonable | Not Applicable | H-1 | 1c, g | (1)e, g | 10e, g | 0.25g | (0.25)g | 2e, g | 0 | 0
Pyrophoric material nondetonable | Not Applicable | H-2 | 4c, g | (4)e, g | 50e, g | 1g | (1)g | 10e, g | 0 | 0
Unstable (reactive) p detonable | 4 3 | H-1 H-1 | 1e, g 1e, g | (1)e, g (1)e, g | 10e, g 10e, g | 0.25g 0.25g | (0.25)g (0.25)g | 2e, g 2e, g | 0.25g 0.25g | (0.25)g (0.25)g
Unstable (reactive) nondetonable | 4 3 2 1 | H-1 H-1 or H-2 H-3 Not Applicable | 1e, g 5d, e 50d, e Not Limited | (1)e, g (5)d, e (50)d, e Not Limited | 10e, g 50d, e 250d, e 750d, e | 0.25g 1d 50d Not Limited | (0.25)g (1)d (50)d Not Limited | 2e, g 10d, e 250d, e Not Limited | 0.25g 1d 10d Not Limited | (0.25)g (1)d (10)d Not Limited
Water-reactive detonable p | 3 2 | H-1 H-1 | 1e, g 1e, g | (1)e, g (1)e, g | Not Applicable | 0.25g 0.25g | (0.25)g (0.25)g | Not Applicable | 0.25g 0.25g | (0.25)g (0.25)g
Water-reactive nondetonable | 3 2 1 | H-2 H-3 Not Applicable | 5d, e 50d, e Not Limited | (5)d, e (50)d, e Not Limited | Not Applicable | 5d 50d Not Limited | (5)d (50)d Not Limited | Not Applicable | 1d 10d Not Limited | (1)d (10)d Not Limited

## 307.1(2)
TABLE 307.1(2)
MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF HAZARDOUS MATERIAL POSING A HEALTH HAZARDa, b, c, i, j
MATERIAL | STORAGEd |  |  | USE-CLOSED SYSTEMSd |  |  | USE-OPEN SYSTEMSd
| Solid pounds | Liquid gallons (pounds)e | Gas SCFe (pounds) | Solid poundse | Liquid gallons (pounds)e | Gas SCFe (pounds) | Solid poundse | Liquid gallons (pounds)e
Corrosive | 5000 | 500 | Gaseous 810f Liquefied (150)h | 5000 | 500 | Gaseous 810f Liquefied (150)h | 1000 | 100
Highly toxic | 10 | (10)h | Gaseous 20g Liquefied (4)g, h | 10 | (10)h | Gaseous 20g Liquefied (4)g, h | 3 | (3)h
Toxic | 500 | (500)h | Gaseous 810f Liquefied (150)f, h | 500 | (500)h | Gaseous 810f Liquefied (150)f, h | 125 | (125)h

## 403.2.4
TABLE 403.2.4
MINIMUM BOND STRENGTH
HEIGHT OF BUILDINGa | SFRM MINIMUM BOND STRENGTH
Up to 420 feet | 430 psf
Greater than 420 feet | 1,000 psf

## 406.5.4
TABLE 406.5.4
OPEN PARKING GARAGES AREA AND HEIGHT
TYPE OF CONSTRUCTION | AREA PER TIER (square feet) | HEIGHT (in tiers)
|  | Ramp access | Mechanical access
Automatic sprinkler system
|  |  | No | Yes
IA | Unlimited | Unlimited | Unlimited | Unlimited
IB | Unlimited | 12 tiers | 12 tiers | 18 tiers
IIA | 50000 | 10 tiers | 10 tiers | 15 tiers
IIB | 50000 | 8 tiers | 8 tiers | 12 tiers
IV | 50000 | 4 tiers | 4 tiers | 4 tiers

## 412.3.1
TABLE 412.3.1
HEIGHT LIMITATIONS FOR
AIRPORT TRAFFIC CONTROL TOWERS
TYPE OF CONSTRUCTION | HEIGHTa (feet)
IA | Unlimited
IB | 240
IIA | 100
IIB | 85
IIIA | 65

## 412.4.6
TABLE 412.4.6
HANGAR FIRE SUPPRESSION REQUIREMENTSa, b, c
MAXIMUM SINGLE FIRE AREA (square feet) | TYPE OF CONSTRUCTION
| IA | IB | IIA | IIB | IIIA | IIIB | IV | VAd | VBd
> 40,001 | Group I | Group I | Group I | Group I | Group I | Group I | Group I | Group I | Group I
40000 | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II
30000 | Group III | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II
20000 | Group III | Group III | Group II | Group II | Group II | Group II | Group II | Group II | Group II
15000 | Group III | Group III | Group III | Group II | Group III | Group II | Group III | Group II | Group II
12000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group II | Group II
8000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group II
5000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group II | Group II

## 412.7
TABLE 412.7
AIRCRAFT MANUFACTURING EXIT ACCESS TRAVEL DISTANCE
HEIGHT (feet)b | MANUFACTURING AREA (sq. ft.)a
| > 150,000 | > 200,000 | > 250,000 | > 500,000 | > 750,000 | >1,000,000
> 25 | 400 | 450 | 500 | 500 | 500 | 500
> 50 | 400 | 500 | 600 | 700 | 700 | 700
> 75 | 400 | 500 | 700 | 850 | 1000 | 1000
> 100 | 400 | 500 | 750 | 1000 | 1250 | 1500

## 414.2.2
TABLE 414.2.2
DESIGN AND NUMBER OF CONTROL AREAS
FLOOR LEVEL |  | PERCENTAGE OF THE MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREAa | NUMBER OF CONTROL AREAS PER FLOORb | FIRE-RESISTANCE RATING FOR FIRE BARRIERS IN HOURSb
Above grade | Higher than 9 | 5 | 1 | 2
| 7–9 | 5 | 2 | 2
| 6 | 12.5 | 2 | 2
| 5 | 12.5 | 2 | 2
| 4 | 12.5 | 2 | 2
| 3 | 50 | 2 | 1
| 2 | 75 | 3 | 1
| 1 | 100 | 4 | 1
Below grade | 1 | 75 | 3 | 1
| 2 | 50 | 2 | 1
| Lower than 2 | Not Allowed | Not Allowed | Not Allowed

## 414.2.5(1)
TABLE 414.2.5(1)
MAXIMUM ALLOWABLE QUANTITY PER INDOOR AND OUTDOOR CONTROL AREA IN GROUP M AND S OCCUPANCIES
NONFLAMMABLE SOLIDS AND NONFLAMMABLE AND NONCOMBUSTIBLE LIQUIDSd, e, f
CONDITION |  | MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA
Materiala | Class | Solids pounds | Liquids gallons
A. Health-hazard materials—nonflammable and noncombustible solids and liquids
Corrosivesb, c | Not Applicable | 9750 | 975
Highly toxics | Not Applicable | 20b, c | 2b, c
Toxicsb, c | Not Applicable | 1000 | 100
B. Physical-hazard materials—nonflammable and noncombustible solids and liquids
1. Oxidizersb, c | 4 | Not Allowed | Not Allowed
| 3 | 1,150g | 115
| 2 | 2,250h | 225
| 1 | 18,000i, j | 18,000i, j
| 4 | Not Allowed | Not Allowed
2. Unstable (reactives)b, c | 3 | 550 | 55
| 2 | 1150 | 115
| 1 | Not Limited | Not Limited
3. Water reactives | 3b, c | 550 | 55
| 2b, c | 1150 | 115
| 1 | Not Limited | Not Limited

## 414.2.5(2)
‡‡‡TABLE 414.2.5(2)
MAXIMUM ALLOWABLE QUANTITY OF FLAMMABLE AND COMBUSTIBLE LIQUIDS
IN WHOLESALE AND RETAIL SALES OCCUPANCIES PER CONTROL AREAa
TYPE OF LIQUID | MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA (gallons)
| Sprinklered in accordance with note b densities and arrangements | Sprinklered in accordance with Tables 5704.3.6.3(4) through 5704.3.6.3(8) and 5704.3.7.5.1 of the New York City Fire Code | Nonsprinklered
Class IA | 60 | 60 | 30
Class IB, IC, II and IIIA | 7,500c | 15,000c | 1600
Class IIIB | Unlimited | Unlimited | 13200

## 414.5.1
TABLE 414.5.1
EXPLOSION CONTROL REQUIREMENTSa, h
MATERIAL | CLASS | EXPLOSION CONTROL METHODS
|  | Barricade construction | Explosion (deflagration) venting or explosion (deflagration) prevention systemsb
HAZARD CATEGORY
Combustible dustsc | — | Not Required | Required
Cryogenic flammables | — | Not Required | Required
Explosives | Division 1.1 Division 1.2 Division 1.3 Division 1.4 Division 1.5 Division 1.6 | Required Required Not Required Not Required Required Required | Not Required Not Required Required Required Not Required Not Required
Flammable gas | Gaseous Liquefied | Not Required Not Required | Required Required
Flammable liquid | IAd IBe | Not Required Not Required | Required Required
Organic peroxides | U I | Required Required | Not Permitted Not Permitted
Oxidizer liquids and solids | 4 | Required | Not Permitted
Pyrophoric gas | — | Not Required | Required
Unstable (reactive) | 4 3 Detonable 3 Nondetonable | Required Required Not Required | Not Permitted Not Permitted Required
Water-reactive liquids and solids | 3 2g | Not Required Not Required | Required Required
SPECIAL USES
Grain processing | — | Not Required | Required
Where explosion hazards existf | Detonation Deflagration | Required Not Required | Not Permitted Required

## 415.6.1
TABLE 415.6.1
MINIMUM SEPARATION DISTANCES FOR BUILDINGS CONTAINING EXPLOSIVE MATERIALSf
QUANTITY OF EXPLOSIVE MATERIALa, d |  | MINIMUM DISTANCE (feet)
|  | Lot linesb and inhabited buildingsc |  | Separation of magazinese
Pounds over | Pounds not over | Barricaded | Unbarricaded
0 | 5 | 70 | 140 | 12
5 | 10 | 90 | 180 | 16
10 | 20 | 110 | 220 | 20
20 | 30 | 125 | 250 | 22
30 | 40 | 140 | 280 | 24
40 | 50 | 150 | 300 | 28
50 | 75 | 170 | 340 | 30
75 | 100 | 190 | 380 | 32
100 | 125 | 200 | 400 | 36
125 | 150 | 215 | 430 | 38
150 | 200 | 235 | 470 | 42
200 | 250 | 255 | 510 | 46
250 | 300 | 270 | 540 | 48
300 | 400 | 295 | 590 | 54
400 | 500 | 320 | 640 | 58
500 | 600 | 340 | 680 | 62
600 | 700 | 355 | 710 | 64
700 | 800 | 375 | 750 | 66
800 | 900 | 390 | 780 | 70
900 | 1000 | 400 | 800 | 72

## 415.6.2
TABLE 415.6.2
DETACHED BUILDING REQUIRED
A DETACHED BUILDING IS REQUIRED WHEN THE QUANTITY OF MATERIAL EXCEEDS THAT LISTED HEREIN
Material | Class | Solids and Liquids (tons)a, b | Gases (cubic feet)a, b
Explosives | Division 1.1 Division 1.2 Division 1.3 Division 1.4 Division 1.4c Division 1.5 Division 1.6 | Maximum Allowable Quantity Maximum Allowable Quantity Maximum Allowable Quantity Maximum Allowable Quantity 1 Maximum Allowable Quantity Maximum Allowable Quantity | Not Applicable
Oxidizers | Class 4 | Maximum Allowable Quantity | Maximum Allowable Quantity
Unstable (reactives) detonable | Class 3 or 4 | Maximum Allowable Quantity | Maximum Allowable Quantity
Oxidizer, liquids and solids | Class 3 Class 2 | 1,200 2,000 | Not Applicable Not Applicable
Organic peroxides | Detonable Class I Class II Class III | Maximum Allowable Quantity Maximum Allowable Quantity 25 50 | Not Applicable Not Applicable Not Applicable Not Applicable
Unstable (reactives) nondetonable | Class 3 Class 2 | 1 25 | 2,000 10,000
Water reactives | Class 3 Class 2 | 1 25 | Not Applicable Not Applicable
Pyrphoric gases | Not Applicable | Not Applicable | 2000

## 415.11.1.1.1
TABLE 415.11.1.1.1
QUANTITY LIMITS FOR HAZARDOUS MATERIALS IN A SINGLE FABRICATION AREA IN GROUP H-5a
HAZARD CATEGORY |  | SOLIDS (pounds per square foot) | LIQUIDS (gallons per square foot) | GAS (cubic feet @ NTP/square foot)
PHYSICAL-HAZARD MATERIALS
Combustible dust |  | Note b | Not Applicable | Not Applicable
Combustible fiber | Loose Baled | Note b Notes b, c | Not Applicable | Not Applicable
Combustible liquid Combination Class | II IIIA IIIB I, II and IIIA | Not Applicable | 0.01 0.02 Not Limited 0.04 | Not Applicable
Cryogenic gas | Flammable Oxidizing | Not Applicable | Not Applicable | Note d 1.25
Explosives |  | Note b | Note b | Note b
Flammable gas | Gaseous Liquefied | Not Applicable | Not Applicable | Note d Note d
Flammable liquid Combination Class Combination Class | IA IB IC IA, IB and IC I, II and IIIA | Not Applicable | 0.0025 0.025 0.025 0.025 0.04 | Not Applicable
Flammable solid |  | 0.001 | Not Applicable | Not Applicable
Organic peroxide | Unclassified detonable Class I Class II Class III Class IV Class V | Note b Note b 0.025 0.1 Not Limited Not limited | Not Applicable | Not Applicable
Oxidizing gas Combination of gaseous and liquefied | Gaseous Liquefied | Not Applicable | Not Applicable | 1.25 1.25 1.25
Oxidizer Combination | Class 4 Class 3 Class 2 Class 1 Class 1, 2, 3 | Note b 0.003 0.003 0.003 0.003 | Note b 0.03 0.03 0.03 0.03 | Not Applicable
Pyrophoric material |  | 0.01 | 0.00125 | Notes d and e
Unstable reactive | Class 4 Class 3 Class 2 Class 1 | Note b 0.025 0.1 Not Limited | Note b 0.0025 0.01 Not Limited | Note b Note b Note b Not Limited
Water reactive | Class 3 Class 2 Class 1 | Note b 0.25 Not Limited | 0.00125 0.025 Not Limited | Not Applicable
HEALTH-HAZARD MATERIALS
Corrosives |  | Not Limited | Not Limited | Not Limited
Highly toxic |  | Not Limited | Not Limited | Note d
Toxics |  | Not Limited | Not Limited | Note d

## 504.3
TABLE 504.3a
ALLOWABLE BUILDING HEIGHT IN FEET ABOVE GRADE PLANE
OCCUPANCY CLASSIFICATION | SEE FOOTNOTES | TYPE OF CONSTRUCTION
|  | TYPE I |  | TYPE II |  | TYPE III |  | TYPE IVj | TYPE V
|  | A | Bi | A | B | A | B | HT | A | B
A-1 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
A-2 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
A-3 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
A-4 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
A-5 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
B | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
E | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
F-1 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60
F-2 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
H-1 | S | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | NP
H-2f | S | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
H-3f | S | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
H-4 | S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60
H-5 | S | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
I-1 | S13D | 60 | 60 | 60 | NP | 60 | 55 | 60 | NP | NP
| S13R | 60 | 60 | 60 | NP | 60 | 55 | 60 | NP | NP
| S | UL | 420 | 85 | NP | 85 | 75 | 85 | NP | NP
I-2 | S | UL | 180 | 85 | 55 | 65 | 55 | 65 | 50 | NP
I-3 | S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | NP
I-4 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
M | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
R-1 | S13R | 60 | 60 | 60 | NP | 60 | NP | 60 | NP | NP
| S | UL | 420 | 85 | NP | 85 | NP | 85 | NP | NP
R-2 | S13R | 60 | 60 | 60 | NP | 60 | 60 | 60 | NP | NP
| S | UL | 420 | 85 | NP | 85 | 75 | 85 | NP | NP
R-3 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50g, h | 40g
| S13D | 60 | 60 | 60 | 60 | 60 | 55 | 60 | 50g, h | 40g
| S13R | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60g, h | 60g
| S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70g, h | 60g
S-1 | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60
S-2d, e | NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
Ue | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60
| NSb, c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
| S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60

## 504.4
TABLE 504.4a, b
ALLOWABLE NUMBER OF STORIES ABOVE GRADE PLANE
OCCUPANCY CLASSIFICATION | SEE FOOTNOTES | TYPE OF CONSTRUCTION
|  | TYPE I |  | TYPE II |  | TYPE III |  | TYPE IVi | TYPE V
|  | A | B | A | B | A | B | HT | A | B
A-1 | NSb, c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2
| S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3
A-2 | NSb, c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2
| S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3
A-3 | NSb, c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2
| S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3
A-4 | NSb, c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2
| S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3
A-5 | NSb, c | UL | UL | UL | UL | UL | UL | 6 | UL | UL
| S | UL | UL | UL | UL | UL | UL | 7 | UL | UL
B | NSb, c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2
| S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3
E | NSb, c | UL | UL | 4 | 3 | 4 | 3 | 6 | 3 | 2
| S | UL | UL | 5 | 4 | 5 | 4 | 7 | 4 | 3
F-1 | NSb, c | UL | 6 | 5 | 3 | 5 | 2 | 5 | 3 | 2
| S | UL | 7 | 6 | 4 | 6 | 3 | 6 | 4 | 3
F-2 | NSb, c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2
| S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3
H-1 | S | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | NP
H-2f | S | UL | 3 | 2 | 1 | 2 | 1 | 2 | 1 | 1
H-3f | S | UL | 6 | 4 | 2 | 4 | 2 | 4 | 2 | 1
H-4 | S | UL | 8 | 6 | 4 | 6 | 4 | 6 | 4 | 3
H-5 | S | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2
I-1 | S13D | 6 | 6 | 6 | NP | 4 | 3 | 4 | NP | NP
| S13R | UL | UL | 6 | NP | 5 | 4 | 5 | NP | NP
| S | UL | UL | 7 | NP | 5 | 4 | 5 | NP | NP
I-2 | S | UL | 7 | 5 | 4 | 5 | 3 | 5 | 3 | NP
I-3 | S | UL | 5 | 5 | 4 | 5 | 3 | 5 | 4 | NP
I-4 | NSb, c | UL | UL | 3 | 3 | 3 | 3 | 3 | 2 | 2
| S | UL | UL | 4 | 4 | 4 | 4 | 4 | 3 | 3
M | NSb, c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2
| S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3
R-1 | S13R | 6 | 6 | 6 | NP | 6 | NP | 6 | NP | NP
| S | UL | UL | 7 | NP | 7 | NP | 7 | NP | NP
R-2 | S13R | 6 | 6 | 6 | NP | 6 | 4 | 6 | NP | NP
| S | UL | UL | 7 | NP | 7 | 4 | 7 | NP | NP
R-3 | NSb, c | X | X | X | X | X | X | X | 3g, h | 3g
| S13D | 6 | 6 | 6 | 3 | 6 | 3 | 6 | 3g, h | 3g
| S13R | 6 | 6 | 6 | 4 | 6 | 4 | 6 | 4g, h | 4g
| S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4g, h | 4g
S-1 | NSb, c | UL | 6 | 5 | 3 | 4 | 3 | 4 | 3 | 2
| S | UL | 7 | 6 | 4 | 5 | 4 | 5 | 4 | 3
S-2d, e | NSb, c | UL | UL | 6 | 3 | 6 | 4 | 6 | 3 | 2
| S | UL | UL | 7 | 4 | 7 | 5 | 7 | 4 | 3
Ue | NSb, c | UL | 5 | 4 | 2 | 3 | 2 | 4 | 2 | 1
| S | UL | 6 | 5 | 3 | 4 | 3 | 5 | 3 | 2

## 506.2
TABLE 506.2a
ALLOWABLE AREA FACTOR (At = NS, S1, S13D, S13R, or SM, as applicable) IN SQUARE FEET
TYPE OF CONSTRUCTION
OCCUPANCY CLASSIFICATION | SEE FOOTNOTES | TYPE I |  | TYPE II |  | TYPE III |  | TYPE IVii | TYPE V
|  | A | B | A | B | A | B |  | A | B
A-1 | NSb, c | UL | UL | 17500 | 10500 | 14700 | 5600 | 15000 | 8400 | 5500
| S1 | UL | UL | 52500 | 31500 | 44100 | 16800 | 45000 | 25200 | 16500
| SM | UL | UL | 35000 | 21000 | 29400 | 11200 | 30000 | 16800 | 11000
A-2 | NSb, c | UL | UL | 17500 | 9500 | 14000 | 5600 | 15000 | 8400 | 5500
| S1 | UL | UL | 52500 | 28500 | 42000 | 16800 | 45000 | 25200 | 16500
| SM | UL | UL | 35000 | 19000 | 28000 | 11200 | 30000 | 16800 | 11000
A-3 | NSb, c | UL | UL | 17500 | 9500 | 14000 | 5600 | 15000 | 8400 | 5500
| S1 | UL | UL | 52500 | 28500 | 42000 | 16800 | 45000 | 25200 | 16500
| SM | UL | UL | 35000 | 19000 | 28000 | 11200 | 30000 | 16800 | 11000
A-4 | NSb, c | UL | UL | 17500 | 9500 | 14000 | 5600 | 15000 | 8400 | 5500
| S1 | UL | UL | 52500 | 28500 | 42000 | 16800 | 45000 | 25200 | 16500
| SM | UL | UL | 35000 | 19000 | 28000 | 11200 | 30000 | 16800 | 11000
A-5 | NSb, c | UL | UL | UL | UL | UL | UL | UL | UL | UL
| S1 | UL | UL | UL | UL | UL | UL | UL | UL | UL
| SM | UL | UL | UL | UL | UL | UL | UL | UL | UL
B | NSb, c | UL | UL | 37500 | 10500 | 28500 | 5600 | 36000 | 8400 | 5500
| S1 | UL | UL | 112500 | 31500 | 85500 | 16800 | 108000 | 25200 | 16500
| SM | UL | UL | 75000 | 21000 | 57000 | 11200 | 72000 | 16800 | 11000
E | NSb, c | UL | UL | 26000 | 10500 | 23500 | 5600 | 25500 | 8400 | 5500
| S1 | UL | UL | 78000 | 31500 | 70500 | 16800 | 76500 | 25200 | 16500
| SM | UL | UL | 52000 | 21000 | 47000 | 11200 | 51000 | 16800 | 11000
F-1 | NSb, c | UL | UL | 12500 | 7500 | 7500 | 3000 | 10000 | 3000 | 1000
| S1 | UL | UL | 37500 | 22500 | 22500 | 9000 | 30000 | 9000 | 3000
| SM | UL | UL | 25000 | 15000 | 15000 | 6000 | 20000 | 6000 | 2000
F-2 | NSb, c | UL | UL | 37500 | 10500 | 28500 | 5600 | 30000 | 8400 | 5500
| S1 | UL | UL | 112500 | 31500 | 85500 | 16800 | 90000 | 25200 | 16500
| SM | UL | UL | 75000 | 21000 | 57000 | 11200 | 60000 | 16800 | 11000
H-1 | NSb, c | 21000 | 16500 | 11000 | 7500 | 9500 | 7000 | 10500 | 7500 | NP
| S1 | 21000 | 16500 | 11000 | 7500 | 9500 | 7000 | 10500 | 7500 | NP
H-2f | NSb, c | 21000 | 16500 | 11000 | 7500 | 9500 | 7000 | 10500 | 7500 | 3000
| S1 | 21000 | 16500 | 11000 | 7500 | 9500 | 7000 | 10500 | 7500 | 3000
| SM | 21000 | 16500 | 11000 | 7500 | 9500 | 7000 | 10500 | 7500 | 3000
H-3f | NSb, c | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25000 | 10000 | 5000
| S1 | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25000 | 10000 | 5000
| SM | UL | 60000 | 26500 | 14000 | 17500 | 13000 | 25000 | 10000 | 5000
H-4 | NSb, c | UL | UL | 37000 | 17500 | 28500 | 17500 | 36000 | 18000 | 6500
| S1 | UL | UL | 112500 | 52500 | 85500 | 52500 | 108000 | 54000 | 19500
| SM | UL | UL | 75000 | 35000 | 57000 | 35000 | 72000 | 36000 | 13000
H-5 | NSb, c | UL | UL | 37500 | 23000 | 28500 | 19000 | 36000 | 18000 | 9000
| S1 | UL | UL | 112500 | 69000 | 85500 | 57000 | 108000 | 54000 | 27000
| SM | UL | UL | 75000 | 46000 | 57000 | 38000 | 72000 | 36000 | 18000
I-1 | NSb, c | UL | UL | 19000 | NP | 16500 | 5600 | 18000 | NP | NP
| S13D | UL | UL | 19000 | NP | 16500 | 5600 | 18000 | NP | NP
| S1 | UL | UL | 57000 | NP | 49500 | 16800 | 54000 | NP | NP
| SM | UL | UL | 38000 | NP | 33000 | 11200 | 36000 | NP | NP
I-2 | NSb, c | UL | UL | 7000 | 3500 | 5000 | 1200 | 6500 | 2000 | NP
| S1 | UL | UL | 21000 | 10500 | 15000 | 3600 | 19500 | 6000 | NP
| SM | UL | UL | 14000 | 7000 | 10000 | 2400 | 13000 | 4000 | NP
I-3 | NSb, c | UL | UL | 7000 | 3500 | 5000 | 1200 | 6500 | 2000 | NP
| S1 | UL | UL | 21000 | 10500 | 15000 | 3600 | 19500 | 6000 | NP
| SM | UL | UL | 14000 | 7000 | 10000 | 2400 | 13000 | 4000 | NP
I-4 | NSb, c | UL | UL | 25500 | 9500 | 23500 | 5600 | 25500 | 8400 | 5500
| S1 | UL | UL | 79500 | 28500 | 70500 | 16800 | 76500 | 25200 | 16500
| SM | UL | UL | 53000 | 19000 | 47000 | 11200 | 51000 | 16800 | 11000
M | NSb, c | UL | UL | 21500 | 7500 | 18500 | 5600 | 14000 | 8400 | 5500
| S1 | UL | UL | 64500 | 22500 | 55500 | 16800 | 42000 | 25200 | 16500
| SM | UL | UL | 43000 | 15000 | 37000 | 11200 | 28000 | 16800 | 11000
R-1 | NSb, c | UL | UL | UL | NP | 24000 | NP | 20500 | NP | NP
| S13R | UL | UL | UL | NP | 24000 | NP | 20500 | NP | NP
| S1 | UL | UL | UL | NP | 72000 | NP | 61500 | NP | NP
| SM | UL | UL | UL | NP | 48000 | NP | 41000 | NP | NP
R-2 | NSb, c | UL | UL | UL | NP | 24000 | 5600 | 20500 | NP | NP
| S13R | UL | UL | UL | NP | 24000 | 5600 | 20500 | NP | NP
| S1 | UL | UL | UL | NP | 72000 | 16800 | 61500 | NP | NP
| SM | UL | UL | UL | NP | 48000 | 11200 | 41000 | NP | NP
R-3 | NSb, c | UL | UL | 17500 | 10500 | 14700 | 5600 | 30000 | 8,400g, h | 5,500g
| S13D | UL | UL | 17500 | 10500 | 14700 | 5600 | 30000 | 8,400g, h | 5,500g
| S13R | UL | UL | 17500 | 10500 | 14700 | 5600 | 30000 | 8,400g, h | 5,500g
| S1 | UL | UL | 52500 | 31500 | 44100 | 16800 | 90000 | 8,400g, h | 5,500g
| SM | UL | UL | 35000 | 21000 | 29400 | 11200 | 60000 | 8,400g, h | 5,500g
S-1 | NSb, c | UL | 48000 | 12000 | 7500 | 7500 | 7500 | 7500 | 5000 | 1000
| S1 | UL | 144000 | 36000 | 22500 | 22500 | 22500 | 22500 | 15000 | 3000
| SM | UL | 96000 | 24000 | 15000 | 15000 | 15000 | 15000 | 10000 | 2000
S-2d, e | NSb, c | UL | UL | 15000 | 10000 | 10000 | 8500 | 10000 | 8400 | 5500
| S1 | UL | UL | 45000 | 30000 | 30000 | 25500 | 30000 | 25200 | 16500
| SM | UL | UL | 30000 | 20000 | 20000 | 17000 | 20000 | 16800 | 11000
Ue | NSb, c | UL | 35000 | 19000 | 8500 | 14000 | 8500 | 18000 | 9000 | 5500
| S1 | UL | 105000 | 57000 | 25500 | 42000 | 25500 | 54000 | 27000 | 16500
| SM | UL | 70000 | 38000 | 17000 | 28000 | 17000 | 36000 | 18000 | 11000

## 508.4
TABLE 508.4
REQUIRED SEPARATION OF OCCUPANCIES (HOURS)
OCCUPANCY | A, E |  | I-1ᵃ, I-3, I-4 |  | I-2 |  | Rᵃ |  | F-2, S-2ᵇ, U |  | Bᵉ |  | F-1 |  | M |  | S-1 |  | H-1 |  | H-2 |  | H-3, H-4 |  | H-5
| S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS
A, E | N | N | 1 | 2 | 2 | NP | 1 | 2 | Nᴿ | 1ᴿ | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | NP | NP | 3 | 4 | 2 | 3 | 2 | NP
I-1ᵃ, I-3, I-4 | — | — | N | N | 2 | NP | 1 | NP | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | NP | NP | 3 | NP | 2 | NP | 2 | NP
I-2 | — | — | — | — | N | N | 2 | NP | 2 | NP | 2 | NP | 2 | NP | 2 | NP | 2 | NP | NP | NP | 3 | NP | 2 | NP | 2 | NP
Rᵃ | — | — | — | — | — | — | N | N | 1ᶜ | 2ᶜ | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | NP | NP | 3 | NP | 2 | NP | 2 | NP
F-2, S-2ᵇ, U | — | — | — | — | — | — | — | — | N | N | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | NP | NP | 3 | 4 | 2 | 3 | 2 | NP
Bᵉ | — | — | — | — | — | — | — | — | — | — | N | N | 2 | 3 | 1 | 2 | 2 | 3 | NP | NP | 2 | 3 | 1 | 2 | 1 | NP
F-1 | — | — | — | — | — | — | — | — | — | — | — | — | N | N | 2 | 3 | 2 | 3 | NP | NP | 2 | 3 | 1 | 2 | 1 | NP
M | — | — | — | — | — | — | — | — | — | — | — | — | — | — | N | N | 2 | 3 | NP | NP | 2 | 3 | 1 | 2 | 1 | NP
S-1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | N | N | NP | NP | 2 | 3 | 1 | 2 | 1 | NP
H-1 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | N | NP | NP | NP | NP | NP | NP | NP
H-2 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | N | NP | 1 | NP | 1 | NP
H-3, H-4 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | 1ᵈ | NP | 1 | NP
H-5 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — | N | NP

## 509
‡‡‡ TABLE 509c
INCIDENTAL USES
ROOM OR AREA | SEPARATION AND/OR PROTECTION
Furnace room where any piece of equipment is over 350,000 Btu per hour input | 2 hour; or 1 hour and provide automatic sprinkler systema
Furnace room where any piece of equipment is 350,000 Btu per hour input or less, except in R-3 occupancy | 1 hour or provide automatic sprinkler systema
Rooms with a high pressure steam or water boiler that exceeds 350,000 Btu per hour input | 2 hour; or 1 hour and provide automatic fire-extinguishing systema
Rooms with a high pressure steam or water boiler that is 350,000 Btu per hour input or less | 1 hour or provide automatic sprinkler systema
Rooms that contain a low pressure steam or water boiler regardless of Btu per hour input | 1 hour or provide automatic sprinkler systema, b
Refrigerant machinery room | 1 hour or provide automatic sprinkler system
Hydrogen fuel gas rooms, not classified as Group H | 2 hours in all occupancies
Incinerator rooms | 2 hours and provide automatic sprinkler system
Paint shops, not classified as Group H, located in occupancies other than Group F | 2 hours; or 1 hour and provide automatic sprinkler system
In Group E occupancies, laboratories and vocational shops not classified as Group H | 1 hour or provide automatic sprinkler system
In Group I-2 occupancies, laboratories not classified as Group H | 1 hour and provide automatic sprinkler system
In ambulatory care facilities, laboratories not classified as Group H | 1 hour or provide automatic sprinkler system
Laundry rooms over 100 square feet | 1 hour or provide automatic sprinkler system
In Group I-2, laundry rooms over 100 square feet | 1 hour
Group I-3 cells and Group I-2 patient rooms equipped with padded surfaces | 1 hour
In Group I-2, physical plant maintenance shops | 1 hour
In ambulatory care facilities or Group I-2 occupancies, waste and linen collection rooms with containers that have an aggregate volume of 10 cubic feet or greater | 1 hour
In other than ambulatory care facilities and Group I-2 occupancies, waste and linen collection rooms over 100 square feet | 1 hour or provide automatic sprinkler system
In ambulatory care facilities or Group I-2 occupancies, storage rooms greater than 100 square feet | 1 hour
Stationary storage battery systems having an energy capacity greater than the threshold quantity specified in Table 608.9.1.1 of the New York City Fire Code | 1 hour in group B, F, M, S and U occupancies; 2 hours in Group A, E, I and R occupancies
Rooms containing fire pumps in non-high-rise buildings | 2 hours; or 1 hour and provide automatic sprinkler system throughout the building
Rooms containing fire pumps in high-rise buildings | 2 hours

## 601
TABLE 601
FIRE-RESISTANCE RATING REQUIREMENTS FOR BUILDING ELEMENTS (HOURS)
BUILDING ELEMENT | TYPE I |  | TYPE II |  | TYPE III |  | TYPE IV | TYPE Vⁱ
| A | B | A | B | A | B | HT | A | B
Primary structural frameᴿ (see Section 202) | 3ᵃ | 2ᵃ,ʲ | 1ʲ | 0 | 1 | 0 | HT | 1 | 0
Bearing walls
Exteriorᵃ,ᶠ,ᵍ | 3 | 2 | 1 | 0 | 2 | 2 | 2 | 1 | 0
Interior | 3ᵃ | 2ᵃ | 1 | 0 | 1 | 0 | 1/HT | 1 | 0
Nonbearing walls and partitions Exterior | See Table 602
Nonbearing walls and partitions Interiorᵈ | 0 | 0 | 0 | 0 | 0 | 0 | See Section 602.4.6 | 0 | 0
Floor constructionʰ and associated secondary members (see Section 202) | 2 | 2 | 1 | 0 | 1 | 0 | HT | 1 | 0
Roof construction and associated secondary members (see Section 202) | 1½,ᶜ | 1ᵇ,ᶜ | 1ᵇ,ᶜ | 0ᶜ | 1ᵇ,ᶜ | 0 | HT | 1ᵇ,ᶜ | 0

## 602
TABLE 602
FIRE-RESISTANCE RATING REQUIREMENTS FOR EXTERIOR WALLS BASED ON FIRE SEPARATION DISTANCEᵃ,ᵉ,ᵍ,ʰ,ʲ
FIRE SEPARATION DISTANCE = X (feet) | TYPE OF CONSTRUCTION | OCCUPANCY GROUP Hᶠ | OCCUPANCY GROUP F-1, M, S-1ᵍ,ⁱ | OCCUPANCY GROUP A, B, E, F-2, I, R, S-2, Uᵇ
X < 5ᶜ | All | 3 | 2 | 1
5 ≤ X < 10 | IA | 3 | 2 | 1
| Others | 2 | 1 | 1
10 ≤ X < 30 | IA, IB | 2 | 1 | 1ᵈ
| IIB, VB | 1 | 0 | 0
| Others | 1 | 1 | 1ᵈ
X ≥ 30 | All | 0 | 0 | 0

## 705.2
TABLE 705.2
MINIMUM SETBACK DISTANCE OF PROJECTION
FIRE SEPARATION DISTANCE (FSD)ᵃ | MINIMUM DISTANCE FROM LINE USED TO DETERMINE FSD
0 feet to 2 feet | Projections not permitted
Greater than 2 feet to less than or equal to 3 feet | 24 inches
Greater than 3 feet to less than 30 feet | 24 inches plus 8 inches for every foot of FSD beyond 3 feet or fraction thereof
30 feet or greater | 20 feet

## 705.8
TABLE 705.8
MAXIMUM AREA OF EXTERIOR WALL OPENINGS BASED ON FIRE SEPARATION DISTANCE AND DEGREE OF OPENING PROTECTIONᵐ
FIRE SEPARATION DISTANCE (feet) | DEGREE OF OPENING PROTECTION | ALLOWABLE AREAᵃ
0 to less than 3ᵇ,ᶜ | Unprotected, Nonsprinklered (UP, NS) | Not Permitted
| Unprotected, Sprinklered (UP, S)ⁱ | Not Permitted
| Protected (P) | Not Permittedʲ,ᵎ
3 to less than 5ᵈ,ᵉ | Unprotected, Nonsprinklered (UP, NS) | Not Permitted
| Unprotected, Sprinklered (UP, S)ⁱ | 15%
| Protected (P) | 15%ⁱ
5 to less than 10ᵉ,ᶠ,ⁿ | Unprotected, Nonsprinklered (UP, NS) | 10%ᵇ
| Unprotected, Sprinklered (UP, S)ⁱ | 25%
| Protected (P) | 25%ⁱ
10 to less than 15ᵉ,ᶠ,ᵍ,ⁿ | Unprotected, Nonsprinklered (UP, NS) | 15%ᵇ
| Unprotected, Sprinklered (UP, S)ⁱ | 45%
| Protected (P) | 45%ⁱ
15 to less than 20ᶠ,ᵍ,ⁿ | Unprotected, Nonsprinklered (UP, NS) | 25%
| Unprotected, Sprinklered (UP, S)ⁱ | 75%
| Protected (P) | 75%ⁱ
20 to less than 25ᶠ,ᵍ,ⁿ | Unprotected, Nonsprinklered (UP, NS) | 45%
| Unprotected, Sprinklered (UP, S)ⁱ | No Limit
| Protected (P) | No Limitⁱ
25 to less than 30ᶠ,ᵍ,ⁿ | Unprotected, Nonsprinklered (UP, NS) | 70%
| Unprotected, Sprinklered (UP, S)ⁱ | No Limit
| Protected (P) | No Limitⁱ
30 or greater | Unprotected, Nonsprinklered (UP, NS) | No Limit
| Unprotected, Sprinklered (UP, S)ⁱ | No Limit
| Protected (P) | No Limit

## 706.4
TABLE 706.4
FIRE WALL FIRE-RESISTANCE RATINGS
GROUP | FIRE-RESISTANCE RATING (hours)
A, B, E, H-4, I, R-1, R-2, U | 3ᵃ
F-1, H-3ᵇ, H-5, M, S-1 | 3
H-1, H-2 | 4ᵇ
F-2, S-2, R-3 | 2

## 707.3.10
TABLE 707.3.10
FIRE-RESISTANCE RATING REQUIREMENTS FOR FIRE BARRIER ASSEMBLIES OR HORIZONTAL ASSEMBLIES BETWEEN FIRE AREAS
OCCUPANCY GROUP | FIRE-RESISTANCE RATING (hours)
H-1, H-2 | 4
F-1, H-3, S-1 | 3
A, B, E, F-2, H-4, H-5, I, M, R, S-2 | 2
U | 1

## 716.3
TABLE 716.3
MARKING FIRE-RATED GLAZING ASSEMBLIES
FIRE TEST STANDARD | MARKING | DEFINITION OF MARKING
ASTM E 119 or UL 263 | W | Meets wall assembly criteria.
NFPA 257 or UL 9 | OH | Meets fire window assembly criteria including the hose stream test.
NFPA 252 or UL 10B or UL 10C | D H T | Meets fire door assembly criteria. Meets fire door assembly hose stream test. Meets 450°F temperature rise criteria for 30 minutes.
| XXX | The time in minutes of the fire resistance or fire protection rating of the glazing assembly.

## 716.5
TABLE 716.5
OPENING FIRE PROTECTION ASSEMBLIES, RATINGS AND MARKINGS
TYPE OF ASSEMBLY | REQUIRED WALL ASSEMBLY RATING (hours) | MINIMUM FIRE DOOR AND FIRE SHUTTER ASSEMBLY RATING (hours) | DOOR VISION PANEL SIZEᵇ | FIRE-RATED GLAZING MARKING DOOR VISION PANELᵈ | MINIMUM SIDELIGHT/TRANSOM ASSEMBLY RATING (hours) |  | FIRE-RATED GLAZING MARKING SIDELIGHT/TRANSOM PANEL
[5 empty] | Fire protection | Fire resistance | Fire protection | Fire resistance
Fire walls, public corridor walls and fire barriers having a required fire-resistance rating greater than 1 hour | 4 | 3 | See Note b | D-H-W-240 | Not Permitted | 4 | Not Permitted | W-240
| 3 | 3ᵃ | See Note b | D-H-W-180 | Not Permitted | 3 | Not Permitted | W-180
| 2 | 1½ | 100 sq. in. | ≤ 100 sq. in. = D-H-90 > 100 sq. in. = D-H-W-90 | Not Permitted | 2 | Not Permitted | W-120
| 1½ | 1½ | 100 sq. in. | ≤ 100 sq. in. = D-H-90 > 100 sq. in. = D-H-W-90 | Not Permitted | 1½ | Not Permitted | W-90
Enclosures for shafts, interior exit stairways and interior exit ramps | 2 | 1½ | 100 sq. in. | ≤ 100 sq. in. = D-H-90 > 100 sq. in. = D-H-T-W-90 | Not Permitted | 2 | Not Permitted | W-120
Horizontal exits in fire wallsᶜ | 4 | 3 | 100 sq. in. | ≤ 100 sq. in. = D-H-180 > 100 sq. in. = D-H-W-240 | Not Permitted | 4 | Not Permitted | W-240
| 3 | 3ᵃ | 100 sq. in. | ≤ 100 sq. in. = D-H-180 > 100 sq. in. = D-H-W-180 | Not Permitted | 3 | Not Permitted | W-180
Fire barriers having a required fire-resistance rating of 1 hour: Enclosures for shafts, exit access stairways, exit access ramps, interior exit stairways and interior exit ramps; and exit passageway walls | 1 | 1 | 100 sq. in.ᶜ | ≤ 100 sq. in. = D-H-60 > 100 sq. in. = D-H-T-W-60 | Not Permitted | 1 | Not Permitted | W-60
Other fire barriers; and public corridor walls | 1 | ¾ | Maximum size tested | D-H | ¾ |  | D-H
Fire partitions: Interior corridor walls | 1 | ¾ | Maximum size tested | D-20 | ¾ᵇ |  | D-H-OH-45
Other fire partitions | 1 | ¾ | Maximum size tested | D-H-45 | ¾ |  | D-H-45
Exterior walls | 3 | 2026-11-02 | 100 sq. in.ᵇ | ≤ 100 sq. in. = D-H-90 > 100 sq. in. = D-H-W-90 | Not Permitted | 3 | Not Permitted | W-180
| 2 | 2026-11-02 | 100 sq. in.ᵇ | ≤ 100 sq. in. = D-H-90 > 100 sq. in. = D-H-W-90 | Not Permitted | 2 | Not Permitted | W-120
| 1 | 2026-03-04 | Maximum size tested | D-H-45 | 2026-03-04 |  | D-H-45
Smoke barriers | 1 | ⅓ | Maximum size tested | D-20 | ¾ |  | D-H-OH-45

## 716.6
TABLE 716.6
FIRE WINDOW ASSEMBLY FIRE PROTECTION RATINGS
TYPE OF WALL ASSEMBLY | REQUIRED WALL ASSEMBLY RATING (hours) | MINIMUM FIRE WINDOW ASSEMBLY RATING (hours) | FIRE-RATED GLAZING MARKING
Interior walls:
Fire walls | All | NPᵃ | W-XXXᵇ
Fire barriers | > 1 1 | NPᵃ NPᵃ | W-XXXᵇ W-XXXᵇ
Incidental use areas (Section 707.3.7), Mixed occupancy separations (Section 707.3.9) | 1 | ¾ | OH-45 or W-60
Fire partitions | 1 | ¾ | OH-45 or W-60
Smoke barriers | 1 | ¾ | OH-45 or W-60
Exterior walls | > 1 1 | 1½ ¾ | OH-90 or W-XXXᵇ OH-45 or W-60
Party wall | All | NP | Not Applicable

## 717.3.2.1
TABLE 717.3.2.1
FIRE DAMPER RATING
TYPE OF PENETRATION | MINIMUM DAMPER RATING (hours)
Less than 3-hour fire-resistance-rated assemblies | 1.5
3-hour or greater fire-resistance-rated assemblies | 3

## 721.1(1)
TABLE 721.1(1)
MINIMUM PROTECTION OF STRUCTURAL PARTS BASED ON TIME PERIODS FOR VARIOUS NONCOMBUSTIBLE INSULATING MATERIALSᵐ
STRUCTURAL PARTS TO BE PROTECTED | ITEM NUMBER | INSULATING MATERIAL USED | MINIMUM THICKNESS OF INSULATING MATERIAL FOR THE FOLLOWING FIRE-RESISTANCE PERIODS (inches)
|  |  | 4 hours | 3 hours | 2 hours | 1 hour
1. Steel columns and all of primary trusses | 1-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 6″ × 6″ or greater (not including sandstone, granite and siliceous gravel).ᵃ | 2½ | 2 | 1½ | 1
| 1-1.2 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 8″ × 8″ or greater (not including sandstone, granite and siliceous gravel).ᵃ | 2 | 1½ | 1 | 1
| 1-1.3 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 12″ × 12″ or greater (not including sandstone, granite and siliceous gravel).ᵃ | 1½ | 1 | 1 | 1
| 1-1.4 | Siliceous aggregate concrete and concrete excluded in Item 1-1.1, members 6″ × 6″ or greater.ᵃ | 3 | 2 | 1½ | 1
| 1-1.5 | Siliceous aggregate concrete and concrete excluded in Item 1-1.1, members 8″ × 8″ or greater.ᵃ | 2½ | 2 | 1 | 1
| 1-1.6 | Siliceous aggregate concrete and concrete excluded in Item 1-1.1, members 12″ × 12″ or greater.ᵃ | 2 | 1 | 1 | 1
| 1-2.1 | Clay or shale brick with brick and mortar fillᵃ | 3¾ | — | — | 2¼
| 1-3.1 | 4″ hollow clay tile in two 2″ layers; ½″ mortar between tile and column; ⅜″ metal mesh 0.046″ wire diameter in horizontal joints; tile fill.ᵃ | 4 | — | — | —
| 1-3.2 | 2″ hollow clay tile; ¾″ mortar between tile and column; ⅜″ metal mesh 0.046″ wire diameter in horizontal joints; limestone concrete fill;ᵇ plastered with ¾″ gypsum plaster. | 3 | — | — | —
| 1-3.3 | 2″ hollow clay tile with outside wire ties 0.08″ diameter at each course of tile or ⅜″ metal mesh 0.046″ diameter wire in horizontal joints; limestone or trap-rock concrete fillᶜ extending 1″ outside column on all sides. | — | — | 3 | —
| 1-3.4 | 2″ hollow clay tile with outside wire ties 0.08″ diameter at each course of tile with or without concrete fill; ¾″ mortar between tile and column. | — | — | — | 2
| 1-4.1 | Cement plaster over metal lath wire tied to ¾″ cold-rolled vertical channels with 0.049″ (No. 18 B.W. gage) wire ties spaced 3″ to 6″ on center. Plaster mixed 1:2 by volume, cement to sand. | — | — | 2½ᵇ | ⅞
| 1-5.1 | Vermiculite concrete, 1:4 mix by volume over paperbacked wire fabric lath wrapped directly around column with additional 2″ × 2″ 0.065″/0.065″ (No. 16/16 B.W. gage) wire fabric placed ¾″ from outer surface. Wire fabric tied with 0.049″ (No. 18 B.W. gage) wire spaced 6″ on center for inner layer and 2″ on center for outer layer. | 2 | — | — | —
| 1-6.1 | Perlite or vermiculite gypsum plaster over metal lath wrapped around column and furred 1¼″ from column flanges. Sheets lapped at ends and tied at 6″ intervals with 0.049″ (No. 18 B.W. gage) tie wire. Plaster pushed through to flanges. | 1½ | 1 | — | —
| 1-6.2 | Perlite or vermiculite gypsum plaster over self-furring metal lath wrapped directly around column, lapped 1″ and tied at 6″ intervals with 0.049″ (No. 18 B.W. gage) wire. | 1¾ | 1⅜ | 1 | —
| 1-6.3 | Perlite or vermiculite gypsum plaster on metal lath applied to ¾″ cold-rolled channels spaced 24″ apart vertically and wrapped flatwise around column. | 1½ | — | — | —
| 1-6.4 | Perlite or vermiculite gypsum plaster over two layers of ½″ plain full-length gypsum lath applied tight to column flanges. Lath wrapped with 1″ hexagonal mesh of No. 20 gage wire and tied with doubled 0.035″ diameter (No. 18 B.W. gage) wire ties spaced 23″ on center. For three-coat work, the plaster mix for the second coat shall not exceed 100 pounds of gypsum to 2½ cubic feet of aggregate for the 3-hour system. | 2½ | 2 | — | —
| 1-6.5 | Perlite or vermiculite gypsum plaster over one layer of ½″ plain full-length gypsum lath applied tight to column flanges. Lath tied with doubled 0.049″ (No. 18 B.W. gage) wire ties spaced 23″ on center and scratch coat wrapped with 1″ hexagonal mesh 0.035″ (No. 20 B.W. gage) wire fabric. For three-coat work, the plaster mix for the second coat shall not exceed 100 pounds of gypsum to 2½ cubic feet of aggregate. | — | 2 | — | —
| 1-7.1 | Multiple layers of ½″ gypsum wallboardᶜ adhesivelyᵈ secured to column flanges and successive layers. Wallboard applied without horizontal joints. Corner edges of each layer staggered. Wallboard layer below outer layer secured to column with doubled 0.049″ (No. 18 B.W. gage) steel wire ties spaced 15″ on center. Exposed corners taped and treated. | — | — | 2 | 1
| 1-7.2 | Three layers of ⅝″ Type X gypsum wallboard.ᶜ First and second layer held in place by ⅜″ diameter by 1⅜″ long ring shank nails with ⁵⁄₁₆″ diameter heads spaced 24″ on center at adjacent layer. Middle layer also secured with metal straps at mid-height and 18″ from each end, and by metal corner bead at each corner held by the metal straps. Third layer attached to corner bead with 1″ long gypsum wallboard screws spaced 12″ on center. | — | — | 1⅞ | —
| 1-7.3 | Three layers of ⅝″ Type X gypsum wallboard,ᶜ each layer screw attached to 1⅝″ steel studs 0.018″ thick (No. 25 carbon sheet steel gage) at each corner of column. Middle layer also secured with 0.049″ (No. 18 B.W. gage) double-strand steel wire ties, 24″ on center. Screws are No. 6 by 1″ spaced 24″ on center for inner layer, No. 6 by 1⅝″ spaced 12″ on center for middle layer and No. 8 by 2¼″ spaced 12″ on center for outer layer. | — | 1⅞ | — | —
| 1-8.1 | Wood-fibered gypsum plaster mixed 1:1 by weight gypsum-to-sand aggregate applied over metal lath. Lath lapped 1″ and tied 6″ on center at all end, edges and spacers with 0.049″ (No. 18 B.W. gage) steel tie wires. Lath applied over ½″ spacers made of ¾″ furring channel with 2″ legs bent around each corner. Spacers located 1″ from top and bottom of member and a maximum of 40″ on center and wire tied with a single strand of 0.049″ (No. 18 B.W. gage) steel tie wires. Corner bead tied to the lath at 6″ on center along each corner to provide plaster thickness. | — | — | 1⅝ | —
| 1-9.1 | Minimum W8×35 wide flange steel column (w/d > 0.75) with each web cavity filled even with the flange tip with normal weight carbonate or siliceous aggregate concrete (3,000 psi minimum compressive strength with 145 pcf ± 3 pcf unit weight). Reinforce the concrete in each web cavity with a minimum No. 4 deformed reinforcing bar installed vertically and centered in the cavity, and secured to the column web with a minimum No. 2 horizontal deformed reinforcing bar welded to the web every 18″ on center vertically. As an alternative to the No. 4 rebar, ¾″ diameter by 3″ long headed studs, spaced at 12″ on center vertically, shall be welded on each side of the web midway between the column flanges. | — | — | — | See Note n
2. Webs or flanges of steel beams and girders | 2-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete (not including sandstone, granite and siliceous gravel) with 3″ or finer metal mesh placed 1″ from the finished surface anchored to the top flange and providing not less than 0.025 square inch of steel area per foot in each direction. | 2 | 1½ | 1 | 1
| 2-1.2 | Siliceous aggregate concrete and concrete excluded in Item 2-1.1 with 3″ or finer metal mesh placed 1″ from the finished surface anchored to the top flange and providing not less than 0.025 square inch of steel area per foot in each direction. | 2½ | 2 | 1½ | 1
| 2-2.1 | Cement plaster on metal lath attached to ¾″ cold-rolled channels with 0.04″ (No. 18 B.W. gage) wire ties spaced 3″ to 6″ on center. Plaster mixed 1:2 ½ by volume, cement to sand. | — | — | 2½ᵇ | ⅞
| 2-3.1 | Vermiculite gypsum plaster on a metal lath cage, wire tied to 0.165″ diameter (No. 8 B.W. gage) steel wire hangers wrapped around beam and spaced 16″ on center. Metal lath ties spaced approximately 5″ on center at cage sides and bottom. | — | ⅞ | — | —
| 2-4.1 | Two layers of ⅝″ Type X gypsum wallboardᶜ are attached to U-shaped brackets spaced 24″ on center. 0.018″ thick (No. 25 carbon sheet steel gage) 1⅝″ deep by 1″ galvanized steel runner channels are first installed parallel to and on each side of the top beam flange to provide a ½″ clearance to the flange. The channel runners are attached to steel deck or concrete floor construction with approved fasteners spaced 12″ on center. U-shaped brackets are formed from members identical to the channel runners. At the bent portion of the U-shaped bracket, the flanges of the channel are cut out so that 1⅝″ deep corner channels can be inserted without attachment parallel to each side of the lower flange. | — | — | 1¼ | —
3. Bonded pretensioned reinforcement in prestressed concreteᵉ | 2-4.2 | Three layers of ⅝″ Type X gypsum wallboardᶜ attached to a steel suspension system as described immediately above utilizing the 0.018″ thick (No. 25 carbon sheet steel gage) 1″ × 2″ lower corner angles. The framing is located so that a 2⅜″ and 2″ space is provided between the inner layer of wallboard and the sides and bottom of the beam, respectively. The mesh is held in position with the No. 6 1⅝″-long screws installed in the vertical leg of the bottom corner angles. | — | 1⅞ | — | —
4. Bonded or unbonded post-tensioned tendons in prestressed concreteᶠ,ⁱ | 3-1.1 | Carbonate, lightweight, sand-lightweight and siliceousᶠ aggregate concrete Beams or girders Solid slabsᵇ | 4ᵍ 2 | 3ᵍ 1½ | 2½ 1½ | 1½ 1
| 4-1.1 | Carbonate, lightweight, sand-lightweight and siliceous aggregate concrete Unrestrained members: Solid slabsᵇ Beams and girdersʲ 8″ wide greater than 12″ wide | — — 3 | 2 4½ 2½ | 1½ 2½ 2 | — 1⅜ 1½
5. Reinforcing steel in reinforced concrete columns, beams girders and trusses | 4-1.2 | Carbonate, lightweight, sand-lightweight and siliceous aggregate Restrained members:ᵎ Solid slabsᵇ Beams and girdersʲ 8″ wide greater than 12″ wide | 1¼ 2½ 2 | 1 2 1¾ | ¾ 1⅜ 1½ | — — —
6. Reinforcing steel in reinforced concrete joistsⁱ | 5-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 12″ or larger, square or round. (Size limit does not apply to beams and girders monolithic with floors.) Siliceous aggregate concrete, members 12″ or larger, square or round. (Size limit does not apply to beams and girders monolithic with floors.) | 1½ 2 | 1½ 1½ | 1½ 1½ | 1½ 1½
| 6-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete. | 1¼ | 1¼ | 1 | ¾
7. Reinforcing and tie rods in floor and roof slabsⁱ | 6-1.2 | Siliceous aggregate concrete. | 1¾ | 1½ | 1 | ¾
| 7-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete. | 1 | 1 | ¾ | ¾
| 7-1.2 | Siliceous aggregate concrete. | 1¼ | 1 | 1 | ¾

## 721.1(2)
‡‡‡ TABLE 721.1(2)
RATED FIRE-RESISTANCE PERIODS FOR VARIOUS WALLS AND PARTITIONS a, o, p
MATERIAL | ITEM NUMBER | CONSTRUCTION | MINIMUM FINISHED THICKNESS FACE-TO-FACEb (inches)
|  |  | 4 hours | 3 hours | 2 hours | 1 hour
1. Brick of clay or shale | 1-1.1 | Solid brick of clay or shaleᶜ | 6 | 4.9 | 3.8 | 2.7
| 1-1.2 | Hollow brick, not filled. | 5 | 4.3 | 3.4 | 2.3
| 1-1.3 | Hollow brick unit wall, grout or filled with perlite vermiculite or expanded shale aggregate. | 6.6 | 5.5 | 4.4 | 3
| 1-2.1 | 4″ nominal thick units not less than 75 percent solid backed with a hat-shaped metal furring channel ¾″ thick formed from 0.021″ sheet metal attached to the brick wall on 24″ centers with approved fasteners, and ½″ Type X gypsum wallboard attached to the metal furring strips with 1″-long Type S screws spaced 8″ on center. | — | — | 5ᵈ | —
2. Combination of clay brick and load-bearing hollow clay tile | 2-1.1 | 4″ solid brick and 4″ tile (not less than 40 percent solid). | — | 8 | — | —
| 2-1.2 | 4″ solid brick and 8″ tile (not less than 40 percent solid). | 12 | — | — | —
3. Concrete masonry units | 3-1.1ᶠ,ᵍ | Expanded slag or pumice. | 4.7 | 4 | 3.2 | 2.1
| 3-1.2ᶠ,ᵍ | Expanded clay, shale or slate. | 5.1 | 4.4 | 3.6 | 2.6
| 3-1.3ᶠ | Limestone, cinders or air-cooled slag. | 5.9 | 5 | 4 | 2.7
| 3-1.4ᶠ,ᵍ | Calcareous or siliceous gravel. | 6.2 | 5.3 | 4.2 | 2.8
4. Solid concreteʰ,ⁱ | 4-1.1 | Siliceous aggregate concrete. | 7 | 6.2 | 5 | 3.5
|  | Carbonate aggregate concrete. | 6.6 | 5.7 | 4.6 | 3.2
|  | Sand-lightweight concrete. | 5.4 | 4.6 | 3.8 | 2.7
|  | Lightweight concrete. | 5.1 | 4.4 | 3.6 | 2.5
5. Glazed or unglazed facing tile, nonload-bearing | 5-1.1 | One 2″ unit cored 15 percent maximum and one 4″ unit cored 25 percent maximum with ¾″ mortar-filled collar joint. Unit positions reversed in alternate courses. | — | 6⅜ | — | —
| 5-1.2 | One 2″ unit cored 15 percent maximum and one 4″ unit cored 40 percent maximum with ¾″ mortar-filled collar joint. Unit positions side with ¾″ gypsum plaster. Two wythes tied together every fourth course with No. 22 gage corrugated metal ties. | — | 6¾ | — | —
| 5-1.3 | One unit with three cells in wall thickness, cored 29 percent maximum. | — | — | 6 | —
| 5-1.4 | One 2″ unit cored 22 percent maximum and one 4″ unit cored 41 percent maximum with ¼″ mortar-filled collar joint. Two wythes tied together every third course with 0.030″ (No. 22 galvanized sheet steel gage) corrugated metal ties. | — | — | 6 | —
| 5-1.5 | One 4″ unit cored 25 percent maximum with ¾″ gypsum plaster on one side. | — | — | 4¾ | —
| 5-1.6 | One 4″ unit with two cells in wall thickness, cored 22 percent maximum. | — | — | — | 4
| 5-1.7 | One 4″ unit cored 30 percent maximum with ¾″ vermiculite gypsum plaster on one side. | — | — | 4½ | —
| 5-1.8 | One 4″ unit cored 39 percent maximum with ¾″ gypsum plaster on one side. | — | — | — | 4½
6. Solid gypsum plaster | 6-1.1 | ¾″ by 0.055″ (No. 16 carbon sheet steel gage) vertical cold-rolled channels, 16″ on center with 2.6-pound flat metal lath applied to one face and tied with 0.049″ (No. 18 B.W. gage) wire at 6″ spacing. Gypsum plaster each side mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 2ᵈ
| 6-1.2 | ¾″ by 0.055″ (No. 16 carbon sheet steel gage) cold-rolled channels 16″ on center with metal lath applied to one face and tied with 0.049″ (No. 18 B.W. gage) wire at 6″ spacing. Perlite or vermiculite gypsum plaster each side. For three-coat work, the plaster mix for the second coat shall not exceed 100 pounds of gypsum to 2½ cubic feet of aggregate for the 1-hour system. | — | — | 2½ᵈ | 2ᵈ
| 6-1.3 | ¾″ by 0.055″ (No. 16 carbon sheet steel gage) vertical cold-rolled channels, 16″ on center with ⅜″ gypsum lath applied to one face and attached with sheet metal clips. Gypsum plaster each side mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 2ᵈ
| 6-2.1 | Studless with ½″ full-length plain gypsum lath and gypsum plaster each side. Plaster mixed 1:1 for scratch coat and 1:2 for brown coat, by weight, gypsum to sand aggregate. | — | — | — | 2ᵈ
| 6-2.2 | Studless with ½″ full-length plain gypsum lath and perlite or vermiculite gypsum plaster each side. | — | — | 2½ᵈ | 2ᵈ
| 6-2.3 | Studless partition with ⅜″ rib metal lath installed vertically adjacent edges tied 6″ on center with No. 18 gage wire ties, gypsum plaster each side mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 2ᵈ
7. Solid perlite and portland cement | 7-1.1 | Perlite mixed in the ratio of 3 cubic feet to 100 pounds of portland cement and machine applied to stud side of 1½″ mesh by 0.058-inch (No. 17 B.W. gage) paper-backed woven wire fabric lath wire-tied to 4″-deep steel trussed wireⁱ studs 16″ on center. Wire ties of 0.049″ (No. 18 B.W. gage) galvanized steel wire 6″ on center vertically. | — | — | 3⅜ᵈ | —
8. Solid neat wood fibered gypsum plaster | 8-1.1 | ¾″ by 0.055-inch (No. 16 carbon sheet steel gage) cold-rolled channels, 12″ on center with 2.5-pound flat metal lath applied to one face and tied with 0.049″ (No. 18 B.W. gage) wire at 6″ spacing. Neat gypsum plaster applied each side. | — | — | 2ᵈ | —
9. Solid wallboard partition | 9-1.1 | One full-length layer ½″ Type X gypsum wallboardᶜ laminated to each side of 1″ full-length V-edge gypsum coreboard with approved laminating compound. Vertical joints of face layer and coreboard staggered not less than 3″. | — | — | 2ᵈ | —
10. Hollow (studless) gypsum wallboard partition | 10-1.1 | One full-length layer of ⅝″ Type X gypsum wallboardᶜ attached to both sides of wood or metal top and bottom runners laminated to each side of 1″ × 6″ full-length gypsum coreboard ribs spaced 24″ on center with approved laminating compound. Ribs centered at vertical joints of face plies and joints staggered 24″ in opposing faces. Ribs may be recessed 6″ from the top and bottom. | — | — | — | 2¼ᵈ
| 10-1.2 | 1″ regular gypsum V-edge full-length backing board attached to both sides of wood or metal top and bottom runners with nails or 1⅜″ drywall screws at 24″ on center. Minimum width of runners 1⅝″. Face layer of ½″ regular full-length gypsum wallboard laminated to outer faces of backing board with approved laminating compound. | — | — | — | 4⅝ᵈ
11. Noncombustible studs—interior partition with plaster each side | 11-1.1 | 3¼″ × 0.044″ (No. 18 carbon sheet steel gage) steel studs spaced 24″ on center. ⅝″ gypsum plaster on metal lath each side mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 4¾ᵈ
| 11-1.2 | 3⅜″ × 0.055″ (No. 16 carbon sheet steel gage) approved nailableᵎ studs spaced 24″ on center. ⅝″ neat gypsum wood-fibered plaster each side over ⅜″ rib metal lath nailed to studs with 6d common nails, 8″ on center. Nails driven 1¼″ and bent over. | — | — | — | 5⅝
| 11-1.3 | 4″ × 0.044″ (No. 18 carbon sheet steel gage) channel-shaped steel studs at 16″ on center. On each side approved resilient clips pressed on to stud flange at 16″ vertical spacing, ¼″ pencil rods snapped into or wire tied onto outer loop of clips, metal lath wire-tied to pencil rods at 6″ intervals, 1″ perlite gypsum plaster, each side. | — | 7⅝ᵈ | — | —
| 11-1.4 | 2½″ × 0.044″ (No. 18 carbon sheet steel gage) steel studs spaced 16″ on center. Wood fibered gypsum plaster mixed 1:1 by weight gypsum to sand aggregate applied on ¾-pound metal lath wire tied to studs, each side. ¾″ plaster applied over each face, including finish coat. | — | — | 4¼ᵈ | —
12. Wood studs interior partition with plaster each side | 12-1.1ʰ,ᵐ | 2″ × 4″ wood studs 16″ on center with ⅝″ gypsum plaster on metal lath. Lath attached by 4d common nails bent over or No. 14 gage by 1¼″ by ¾″ crown width staples spaced 6″ on center. Plaster mixed 1:1½ for scratch coat and 1:3 for brown coat, by weight, gypsum to sand aggregate. | — | — | — | 5⅜
| 12-1.2ʲ | 2″ × 4″ wood studs 16″ on center with metal lath and ⅞″ neat wood-fibered gypsum plaster each side. Lath attached by 6d common nails, 7″ on center. Nails driven 1¼″ and bent over. | — | — | 5½ᵈ | —
| 12-1.3ʲ | 2″ × 4″ wood studs 16″ on center with ⅜″ perforated or plain gypsum lath and ½″ gypsum plaster each side. Lath nailed with 1⅜″ by No. 13 gage by ¹⁹⁄₆₄″ head plasterboard blued nails, 4″ on center. Plaster mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 5¼
| 12-1.4ʲ | 2″ × 4″ wood studs 16″ on center with ⅜″ Type X gypsum lath and ½″ gypsum plaster each side. Lath nailed with 1⅜″ by No. 13 gage by ¹⁹⁄₆₄″ head plasterboard blued nails, 5″ on center. Plaster mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 5¼
13. Noncombustible studs—interior partition with gypsum wallboard each side | 13-1.1 | 0.018″ (No. 25 carbon sheet steel gage) channel-shaped studs 24″ on center with one full-length layer of ⅝″ Type X gypsum wallboardᶜ applied vertically attached with 1″ long No. 6 drywall screws to each stud. Screws are 8″ on center around the perimeter and 12″ on center on the intermediate stud. Where applied horizontally, the Type X gypsum wallboard shall be attached to 3⅝″ studs and the horizontal joints shall be staggered with those on the opposite side. Screws for the horizontal application shall be 8″ on center at vertical edges and 12″ on center at intermediate studs. | — | — | — | 2⅞ᵈ
| 13-1.2 | 0.018″ (No. 25 carbon sheet steel gage) channel-shaped studs 25″ on center with two full-length layers of ½″ Type X gypsum wallboardᶜ applied vertically each side. First layer attached with 1″-long, No. 6 drywall screws, 8″ on center around the perimeter and 12″ on center on the intermediate stud. Second layer applied with vertical joints offset one stud space from first layer using 1⅝″-long, No. 6 drywall screws spaced 9″ on center along vertical joints, 12″ on center at intermediate studs and 24″ on center along top and bottom runners. | — | — | 3⅝ᵈ | —
| 13-1.3 | 0.055″ (No. 16 carbon sheet steel gage) approved nailable metal studsᶜ 24″ on center with full-length ⅝″ Type X gypsum wallboardᶜ applied vertically and nailed 7″ on center with 6d cement-coated common nails. Approved metal fastener grips used with nails at vertical butt joints along studs. | — | — | — | 4⅜
14. Wood studs—interior partition with gypsum wallboard each side | 14-1.1ʰ,ᵐ | 2″ × 4″ wood studs 16″ on center with two layers of ⅜″ regular gypsum wallboardᶜ each side, 4d coolerᵎ or wallboardᵎ nails at 8″ on center first layer, 5d coolerᵎ or wallboardᵎ nails at 8″ on center second layer with laminating compound between layers, joints staggered. First layer applied full length vertically, second layer applied horizontally or vertically. | — | — | — | 5
| 14-1.2ʲ,ᵐ | 2″ × 4″ wood studs 16″ on center with two layers ½″ regular gypsum wallboardᶜ applied vertically or horizontally each sideᵎ, joints staggered. Nail base layer with 5d coolerᵎ or wallboardᵎ nails at 8″ on center face layer with 8d coolerᵎ or wallboardᵎ nails at 8″ on center. | — | — | — | 5½
| 14-1.3ʲ,ᵐ | 2″ × 4″ wood studs 24″ on center with ⅝″ Type X gypsum wallboardᶜ applied vertically or horizontally nailed with 6d coolerᵎ or wallboardᵎ nails at 7″ on center with end joints on nailing members. Stagger joints each side. | — | — | — | 4¾
| 14-1.4ʲ | 2″ × 4″ fire-retardant-treated wood studs spaced 24″ on center with one layer of ⅝″ Type X gypsum wallboardᶜ applied with face paper grain (long dimension) parallel to studs. Wallboard attached with 6d coolerᵎ or wallboardᵎ nails at 7″ on center. | — | — | — | 4¾ᵈ
| 14-1.5ʲ,ᵐ | 2″ × 4″ wood studs 16″ on center with two layers ⅝″ Type X gypsum wallboardᶜ each side. Base layers applied vertically and nailed with 6d coolerᵎ or wallboardᵎ nails at 9″ on center. Face layer applied vertically or horizontally and nailed with 8d coolerᵎ or wallboardᵎ nails at 7″ on center. For nail-adhesive application, base layers are nailed 6″ on center. Face layers applied with coating of approved wallboard adhesive and nailed 12″ on center. | — | — | — | 6
| 14-1.6ʲ | 2″ × 3″ fire-retardant-treated wood studs spaced 24″ on center with one layer of ⅝″ Type X gypsum wallboardᶜ applied with face paper grain (long dimension) at right angles to studs. Wallboard attached with 6d cement-coated box nails spaced 7″ on center. | — | — | — | 3⅝ᵈ
| 15-1.1ʰ,ᵐ | Exterior surface with ¾″ drop siding over ½″ gypsum sheathing on 2″ × 4″ wood studs at 16″ on center, interior surface treatment as required for 1-hour-rated exterior or interior 2″ × 4″ wood stud partitions. Gypsum sheathing nailed with 1¾″ by No. 11 gage by ⁷⁄₁₆″ head galvanized nails at 8″ on center. Siding nailed with 7d galvanized smooth box nails. | — | — | — | Varies
| 15-1.2ʲ,ᵐ | 2″ × 4″ wood studs 16″ on center with metal lath and ¾″ cement plaster on each side. Lath attached with 6d common nails 7″ on center driven to 1″ minimum penetration and bent over. Plaster mix 1:4 for scratch coat and 1:5 for brown coat, by volume, cement to sand. | — | — | — | 5⅜
15. Exterior or interior walls | 15-1.3ʲ,ᵐ | 2″ × 4″ wood studs 16″ on center with ⅞″ cement plaster (measured from the face of studs) on the exterior surface with interior surface treatment as required for interior wood stud partitions in this table. Plaster mix 1:4 for scratch coat and 1:5 for brown coat, by volume, cement to sand. | — | — | — | Varies
| 15-1.4 | 3⅝″ No. 16 gage noncombustible studs 16″ on center with ⅞″ cement plaster (measured from the face of the studs) on the exterior surface with interior surface treatment as required for interior, nonbearing, noncombustible stud partitions in this table. Plaster mix 1:4 for scratch coat and 1:5 for brown coat, by volume, cement to sand. | — | — | — | Variesᵈ
| 15-1.5ᵐ | 2¼″ × 3¾″ clay face brick with cored holes over ½″ gypsum sheathing on exterior surface of 2″ × 4″ wood studs at 16″ on center and two layers ⅝″ Type X gypsum wallboardᶜ on interior surface. Sheathing placed horizontally or vertically with vertical joints over studs nailed 6″ on center with 1¾″ × No. 11 gage by ⁷⁄₁₆″ head galvanized nails. Inner layer of wallboard placed horizontally or vertically and nailed 8″ on center with 6d coolerᵎ or wallboardᵎ nails. Outer layer of wallboard placed horizontally or vertically and nailed 8″ on center with 8d coolerᵎ or wallboardᵎ nails. Joints staggered with vertical joints over studs. Outer layer joints taped and finished with compound. Nail heads covered with joint compound. 0.035 inch (No. 20 galvanized sheet gage) corrugated galvanized steel wall ties ¾″ by ⅝″ attached to each stud with two 8d coolerᵎ or wallboardᵎ nails every sixth course of bricks. | — | — | 10 | —
| 15-1.6ʲ,ᵐ | 2″ × 6″ fire-retardant-treated wood studs 16″ on center. Interior face has two layers of ⅝″ Type X gypsum with the base layer placed vertically and attached with 6d box nails 12″ on center. The face layer is placed horizontally and attached with 8d box nails 8″ on center at joints and 12″ on center elsewhere. The exterior face has a base layer of ⅝″ Type X gypsum sheathing placed vertically with 6d box nails 8″ on center at joints and 12″ on center elsewhere. An approved building paper is next applied, followed by self-furred exterior lath attached with 2½″, No. 12 gage galvanized roofing nails with ⅜″ diameter head and spaced 6″ on center along each stud. Cement plaster consisting of a ½″ brown coat is then applied. The scratch coat is mixed in the proportion of 1:3 by weight, cement to sand with 10 pounds of hydrated lime and 3 pounds of approved additives or admixtures per sack of cement. The brown coat is mixed in the proportion of 1:4 by weight, cement to sand with the same amounts of hydrated lime and approved additives or admixtures used in the scratch coat. | — | — | 8¼ | —
| 15-1.7ʲ,ᵐ | 2″ × 6″ wood studs 16″ on center. The exterior face has a layer of ⅝″ Type X gypsum sheathing placed vertically with 6d box nails 8″ on center at joints and 12″ on center elsewhere. An approved building paper is next applied, followed by 1″ by No. 18 gage self-furred exterior lath attached with 2½″ long galvanized roofing nails spaced 6″ on center along each stud. Cement plaster consisting of a ½″ scratch coat, a bonding agent and a ½″ brown coat and a finish coat is then applied. The interior is covered with ⅜″ gypsum lath with 1″ hexagonal mesh of 0.035 inch (No. 20 B.W. gage) woven wire lath furred out ⁵⁄₁₆″ and 1″ perlite or vermiculite gypsum plaster. | — | — | 8⅜ | —
| 15-1.8ʲ,ᵐ | 2″ × 6″ wood studs 16″ on center. The exterior face has a layer of ⅝″ Type X gypsum sheathing placed vertically with 6d box nails 8″ on center at joints and 12″ on center elsewhere. An approved building paper is next applied, followed by 1½″ by No. 17 gage self-furred exterior lath attached with 8d by 2½″ long galvanized roofing nails spaced 6″ on center along each stud. Cement plaster consisting of a ½″ scratch coat, and a ½″ brown coat is then applied. The interior is covered with ⅜″ gypsum lath with 1″ hexagonal mesh of No. 20 gage woven wire lath furred out ⁵⁄₁₆″ and 1″ perlite or vermiculite gypsum plaster. | — | — | 8⅜ | —
| 15-1.9 | 4″ No. 18 gage, nonload-bearing metal studs, 16″ on center, with 1″ portland cement lime plaster (measured from the back side of the ¾-pound expanded metal lath) on the exterior surface. Interior surface to be covered with 1″ of gypsum plaster on ¾-pound expanded metal lath proportioned by weight—1:2 for scratch, for brown, gypsum to sand. Lath on one side of the partition fastened to ¼″ diameter pencil rods supported by No. 20 gage metal clips, located 16″ on center, vertically, on each stud. 3″ thick mineral fiber insulating batts friction fitted between the studs. | — | — | 6½ᵈ | —
| 15-1.10 | Steel studs 0.060″ thick, 4″ deep or 6″ at 16″ or 24″ centers, with ½″ Glass Fiber Reinforced Concrete (GFRC) on the exterior surface. GFRC is attached with flex anchors at 24″ on center, with 5″ leg welded to studs with two ½″-long flare-bevel welds, and 4’ foot attached to the GFRC skin with ⅝″ thick GFRC bonding pads that extend 2½″ beyond the flex anchor foot on both sides. Interior surface to have two layers of ½″ Type X gypsum wallboard.ᶜ The first layer of wallboard to be attached with 1″-long Type S buglehead screws spaced 24″ on center and the second layer is attached with 1⅜″-long Type S screws spaced at 12″ on center. Cavity is to be filled with 5″ of 4 pcf (nominal) mineral fiber batts. GFRC has 1½″ returns packed with mineral fiber and caulked on the exterior. | — | — | 6½ | —
| 15-1.11 | Steel studs 0.060″ thick, 4″ deep or 6″ at 16″ or 24″ centers, respectively, with ½″ Glass Fiber Reinforced Concrete (GFRC) on the exterior surface. GFRC is attached with flex anchors at 24″ on center, with 5″ leg welded to studs with two ½″-long flare-bevel welds, and 4’ foot attached to the GFRC skin with ⅝″-thick GFRC bonding pads that extend 2½″ beyond the flex anchor foot on both sides. Interior surface to have one layer of ⅜″ Type X gypsum wallboardᶜ, attached with 1¼″-long Type S buglehead screws spaced 12″ on center. Cavity is to be filled with 5″ of 4 pcf (nominal) mineral fiber batts. GFRC has 1½″ returns packed with mineral fiber and caulked on the exterior. | — | — | — | 6⅜
| 15-1.12ᵍ | 2″ × 6″ wood studs at 16″ with double top plates, single bottom plate; interior and exterior sides covered with ⅝″ Type X gypsum wallboard,ᶜ 4’ wide, applied horizontally or vertically with vertical joints over studs, and fastened with 2¼″ Type S drywall screws, spaced 12″ on center. Cavity to be filled with 5½″ mineral wool insulation. | — | — | — | 6¾
| 15-1.13ᵍ | 2″ × 6″ wood studs at 16″ with double top plates, single bottom plate; interior and exterior sides covered with ⅝″ Type X gypsum wallboard,ᶜ 4’ wide, applied vertically with all joints over framing or blocking, and fastened with 2¼″ Type S drywall screws, spaced 12″ on center. R-19 mineral fiber insulation installed in stud cavity. | — | — | — | 6¾
| 15-1.14ᵍ | 2″ × 6″ wood studs at 16″ with double top plates, single bottom plate; interior and exterior sides covered with ⅝″ Type X gypsum wallboard,ᶜ 4’ wide, applied horizontally or vertically with vertical joints over studs, and fastened with 2¼″ Type S drywall screws, spaced 7″ on center. | — | — | — | 6¾
| 15-1.15ᵍ | 2″ × 4″ wood studs at 16″ with double top plates, single bottom plate; interior and exterior sides covered with ⅝″ Type X gypsum wallboard and sheathing, respectively, 4’ wide, applied horizontally or vertically with vertical joints over studs, and fastened with 2¼″ Type S drywall screws, spaced 12″ on center. Cavity to be filled with 3½″ mineral wool insulation. | — | — | — | 4¾
| 15-1.16ᵍ | 2″ × 6″ wood studs at 24″ centers with double top plates, single bottom plate; interior and exterior side covered with two layers of ⅝″ Type X gypsum wallboard,ᶜ 4’ wide, applied horizontally with vertical joints. Base layer fastened with 2¼″ Type S drywall screws, spaced 24″ on center, and face layer fastened with Type S drywall screws, spaced 8″ on center, wallboard joints covered with paper tape and joint compound, fastener heads covered with joint compound. Cavity to be filled with 5½″ mineral wool insulation. | — | 7¾ | — | —
| 15-2.1ᵍ | 3⅝″ No. 16 gage steel studs at 24″ on center or 2″ × 4″ wood studs at 24″ on center. Metal lath attached to the exterior side of studs with minimum 1″ long No. 6 drywall screws at 6″ on center and covered with minimum ¾″ thick portland cement plaster. Thin veneer brick units of clay or shale complying with ASTM C 1088, Grade TBS or better, installed in running bond in accordance with Section 1405.10. Combined total thickness of the portland cement plaster, mortar and thin veneer brick units shall be not less than 1¼″. Interior side covered with one layer of ⅝″ thick Type X gypsum wallboard attached to studs with 1″ long No. 6 drywall screws at 12″ on center. | — | — | — | 6
| 15-2.2ᵍ | 3⅝″ No. 16 gage steel studs at 24″ on center or 2″ × 4″ wood studs at 24″ on center. Metal lath attached to the exterior side of studs with minimum 1″ long No. 6 drywall screws at 6″ on center and covered with minimum ¾″ thick portland cement plaster. Thin veneer brick units of clay or shale not less than 2″ thick complying with ASTM C 216 installed in accordance with Section 1405.10 with a minimum 1″ airspace. Interior side covered with two layers of ⅝″ thick Type X gypsum wallboard. Bottom layer attached to studs with 1″ long No. 6 drywall screws at 24″ on center. Top layer attached to studs with 1⅝″ long No. 6 drywall screws at 12″ on center. | — | — | 6⅞ | —
| 15-2.3ᵍ | 3⅝″ No. 16 gage steel studs at 16″ on center or 2″ x 4″ wood studs at 16″ on center. Where metal lath is used, attach to the exterior side of studs with minimum 1″ long No. 6 drywall screws at 6″ on center. Brick units of clay or shale not less than 2⅝″ thick complying with ASTM C 216 installed in accordance with Section 1405.6 with a minimum 1″ airspace. Interior side covered with one layer of ⅝″ thick Type X gypsum wallboard attached to studs with 1″ long No. 6 drywall screws at 12″ on center. | — | — | — | 7⅞
| 15-2.4ᵍ | 3⅝″ No. 16 gage steel studs at 16″ on center or 2″ x 4″ wood studs at 16″ on center. Where metal lath is used, attach to the exterior side of studs with minimum 1″ long No. 6 drywall screws at 6″ on center. Brick units of clay or shale not less than 2⅝″ thick complying with ASTM C 216 installed in accordance with Section 1405.6 with a minimum 1″ airspace. Interior side covered with two layers of ⅝″ thick Type X gypsum wallboard. Bottom layer attached to studs with 1″ long No. 6 drywall screws at 24″ on center. Top layer attached to studs with 1⅝″ long No. 6 drywall screws at 12″ on center. | — | — | 8½ | —
16. Exterior walls rated for fire resistance from the inside only in accordance with Section 705.5. | 16-1.1ᵍ | 2″ × 4″ wood studs at 16″ centers with double top plates, single bottom plate; interior side covered with ⅝″ Type X gypsum wallboard,ᶜ 4’ wide, applied horizontally unblocked, and fastened with 2¼″ Type S drywall screws, spaced 12″ on center, wallboard joints covered with paper tape and joint compound, fastener heads covered with joint compound. Exterior covered with ⅜″ wood structural panels, applied vertically, horizontal joints blocked and fastened with 6d common nails (bright) — 12″ on center in the field, and 6″ on center panel edges. Cavity to be filled with 3½″ mineral wool insulation. Rating established for exposure from interior side only. | — | — | — | 4½
| 16-1.2ᵍ | 2″ × 6″ wood studs at 16″ centers with double top plates, single bottom plate; interior side covered with ⅝″ Type X gypsum wallboard,ᶜ 4’ wide, applied horizontally or vertically with vertical joints over studs and fastened with 2¼″ Type S drywall screws, spaced 12″ on center, wallboard joints covered with paper tape and joint compound, fastener heads covered with joint compound, exterior side covered with ⁷⁄₁₆″ wood structural panels fastened with 6d common nails (bright) spaced 12″ on center in the field and 6″ on center along the panel edges. Cavity to be filled with 5½″ mineral wool insulation. Rating established from the gypsum-covered side only. | — | — | — | 6⁹⁄₁₆
| 16-1.3ᵍ | 2″ x 6″ wood studs at 16″ centers with double top plates, single bottom plates; interior side covered with ⅝″ Type X gypsum wallboard,ᶜ 4’ wide, applied vertically with all joints over framing or blocking and fastened with 2¼″ Type S drywall screws spaced 7″ on center. Joints to be covered with tape and joint compound. Exterior covered with ⅜″ wood structural panels, applied vertically with edges over framing or blocking and fastened with 6d common nails (bright) at 12″ on center in the field and 6″ on center panel edges. R-19 mineral fiber insulation installed in stud cavity. Rating established from the gypsum-covered side only. | — | — | — | 6½

## 721.1(3)
‡‡‡ TABLE 721.1(3)
MINIMUM PROTECTION FOR FLOOR AND ROOF SYSTEMS a, q
FLOOR OR ROOF CONSTRUCTION | ITEM NUMBER | CEILING CONSTRUCTION | THICKNESS OF FLOOR OR ROOF SLAB (inches) |  |  |  | MINIMUM THICKNESS OF CEILING (inches)
|  |  | 4 hours | 3 hours | 2 hours | 1 hour | 4 hours | 3 hours | 2 hours | 1 hour
1. Siliceous aggregate concrete | 1-1.1 | Slab (no ceiling required). Minimum cover over nonprestressed reinforcement shall be not less than ¾ inch.ᵇ | 7 | 6.2 | 5 | 3.5 | — | — | — | —
2. Carbonate aggregate concrete | 2-1.1 | Slab (no ceiling required). Minimum cover over nonprestressed reinforcement shall be not less than ¾ inch.ᵇ | 6.6 | 5.7 | 4.6 | 3.2 | — | — | — | —
3. Sand-lightweight concrete | 3-1.1 | Slab (no ceiling required). Minimum cover over nonprestressed reinforcement shall be not less than ¾ inch.ᵇ | 5.4 | 4.6 | 3.8 | 2.7 | — | — | — | —
4. Lightweight concrete | 4-1.1 | Slab (no ceiling required). Minimum cover over nonprestressed reinforcement shall be not less than ¾ inch.ᵇ | 5.1 | 4.4 | 3.6 | 2.5 | — | — | — | —
5. Reinforced concrete | 5-1.1 | Slab with suspended ceiling of vermiculite gypsum plaster over metal lath attached to ¾″ cold-rolled channels spaced 12″ on center. Ceiling located 6″ minimum below joists. | 3 | 2 | — | — | 1 | ¾ | — | —
| 5-2.1 | ⅜″ Type X gypsum wallboardᶜ attached to 0.018 inch (No. 25 carbon sheet steel gage) by ⅞″ deep by 2⅝″ hat-shaped galvanized steel channels with 1″-long No. 6 screws. The channels are spaced 24″ on center, span 35″ and are supported along their length at 35″ intervals by 0.033-inch (No. 21 galvanized sheet gage) galvanized steel flat strap hangers having formed edges that engage the lips of the channel. The strap hangers are attached to the side of the concrete joists with ⁵⁄₃₂″ by 1¼″ long power-driven fasteners. The wallboard is installed with the long dimension perpendicular to the channels. End joints occur on channels and supplementary channels are installed parallel to the main channels, 12″ each side, at end joint occurrences. The finished ceiling is located approximately 12″ below the soffit of the floor slab. | — | — | 2½ | — | — | — | ⅝ | —
6. Steel joists constructed with a poured reinforced concrete slab on metal lath forms or steel form unitsᵈ, ᵉ | 6-1.1 | Gypsum plaster on metal lath attached to the bottom cord with single No. 16 gage or doubled No. 18 gage wire ties spaced 6″ on center. Plaster mixed 1:2 for scratch coat, 1:3 for brown coat, by weight, gypsum-to-sand aggregate for 2-hour system. For 3-hour system plaster is neat. | — | — | 2½ | 2¼ | — | — | ¾ | ⅝
| 6-2.1 | Vermiculite gypsum plaster on metal lath attached to the bottom chord with single No. 16 gage or doubled 0.049-inch (No. 18 B.W. gage) wire ties 6″ on center. | — | 2 | — | — | — | ⅝ | — | —
| 6-3.1 | Cement plaster over metal lath attached to the bottom chord of joists with single No. 16 gage or doubled 0.049-inch (No. 18 B.W. gage) wire ties spaced 6″ on center. Plaster mixed 1:2 for scratch coat, 1:3 for brown coat for 1-hour system, 1:1 for scratch coat, 1:1½ for brown coat for 2-hour system, by weight, cement to sand. | — | — | — | 2 | — | — | — | ⅝ᶠ
| 6-4.1 | Ceiling of ⅝″ Type X wallboardᶜ attached to ⅞″ deep by 2⅝″ by 0.02 1 inch (No. 25 carbon sheet steel gage) hat-shaped furring channels 12″ on center with 1″ long No. 6 wallboard screws at 8″ on center. Channels wire tied to bottom chord of joists with doubled 0.049 inch (No. 18 B.W. gage) wire or suspended below joists on wire hangers.ᵍ | — | — | 2½ | — | — | — | ⅝ | —
7. Reinforced concrete slabs and joists with hollow clay tile fillers laid end to end in rows 2½″ or more apart; reinforcement placed between rows and concrete cast around and over tile. | 6-5.1 | Wood-fibered gypsum plaster mixed 1:1 by weight gypsum to sand aggregate applied over metal lath. Lath tied 6″ on center to ¾″ channels spaced 13½″ on center. Channels secured to joists at each intersection with two strands of 0.049 inch (No. 18 B.W. gage) galvanized wire. | — | — | 2½ | — | — | — | ¾ | —
7. Reinforced concrete slabs and joists with hollow clay tile fillers laid end to end in rows 2½″ or more apart; reinforcement placed between rows and concrete cast around and over tile. | 7-1.1 | ⅝″ gypsum plaster on bottom of floor or roof construction. | — | — | 8ʰ | — | — | — | ⅝ | —
| 7-1.2 | None | — | — | — | 5½ʲ | — | — | — | —
9. 3″ deep cellular steel deck with concrete slab on top. Slab thickness measured to top. | 8-1.1 | Vermiculite gypsum plaster on metal lath attached to ¾″ cold-rolled channels with 0.049″ (No. 18 B.W. gage) wire ties spaced 6″ on center. | 2½ʲ | — | — | — | ¾ | — | — | —
10. 1½″-deep steel roof deck on steel framing. Insulation board, 30 pcf density, composed of wood fibers with cement binders of thickness shown bonded to deck with unified asphalt adhesive. Covered with a Class A or B roof covering. | 9-1.1 | Suspended ceiling of vermiculite gypsum plaster base coat and vermiculite acoustical plaster on metal lath attached at 6″ intervals to ¾″ cold-rolled channels spaced 12″ on center and secured to 1½″ cold-rolled channels spaced 36″ on center with 0.065″ (No. 16 B.W. gage) wire. 1½″ channels supported by No. 8 gage wire hangers at 36″ on center. Beams within envelope and with a 2½″ airspace between beam soffit and lath have a 4-hour rating. | 2½ | — | — | — | 1⅜ᵎ | — | — | —
11. 1½″-deep steel roof deck on steel-framing wood fiber insulation board, 17.5 pcf density on top applied over a 15-lb asphalt-saturated felt. Class A or B roof covering. | 10-1.1 | Ceiling of gypsum plaster on metal lath. Lath attached to ¾″ furring channels with 0.049″ (No. 18 B.W. gage) wire ties spaced 6″ on center. ¾″ channel saddle tied to 2″ channels with doubled 0.065″ (No. 16 B.W. gage) wire ties. 2″ channels spaced 36″ on center suspended 2″ below steel framing and saddle-tied with 0.165″ (No. 8 B.W. gage) wire. Plaster mixed 1:2 by weight, gypsum-to-sand aggregate. | — | — | 1⅞ | 1 | — | — | ¾ʲ | ¾ʲ
12. 1½″ deep steel roof deck on steel-framing insulation of rigid board consisting of expanded perlite and fibers impregnated with integral asphalt waterproofing; density 9 to 12 pcf secured to metal roof deck by ½″ wide ribbons of waterproof, cold-process liquid adhesive spaced 6″ apart. Steel joist or light steel construction with metal roof deck, insulation, and Class A or B built-up roof covering.ᵉ | 11-1.1 | Ceiling of gypsum plaster on metal lath. Lath attached to ¾″ furring channels with 0.049″ (No. 18 B.W. gage) wire ties spaced 6″ on center. ¾″ channels saddle tied to 2″ channels with doubled 0.065″ (No. 16 B.W. gage) wire ties. 2″ channels spaced 36″ on center suspended 2″ below steel framing and saddle tied with 0.165″ (No. 8 B.W. gage) wire. Plaster mixed 1:2 for scratch coat and 1:3 for brown coat, by weight, gypsum-to-sand aggregate for 1-hour system. For 2-hour system, plaster mix is 1:2 by weight, gypsum-to-sand aggregate. | — | — | 1½ | 1 | — | — | ⅞ᵍ | ¾ʲ
13. Double wood floor over wood joists spaced 16″ on center.ᵐ, ᵎ | 12-1.1 | Gypsum-vermiculite plaster on metal lath wire tied at 6″ intervals to ¾″ furring channels spaced 12″ on center and wire tied to 2″ runner channels spaced 32″ on center. Runners wire tied to bottom chord of steel joists. | — | — | 1 | — | — | — | ⅞ | —
13. Double wood floor over wood joists spaced 16″ on center.ᵐ, ᵎ | 13-1.1 | Gypsum plaster over ⅜″ Type X gypsum lath. Lath initially applied with not less than four 1⅜″ by No. 13 gage by ¹⁹⁄₆₄″ head plasterboard blued nails per bearing. Continuous stripping over lath along all joist lines. Stripping consists of 3″ wide strips of metal lath attached by 1½″ by No. 11 gage by ½″ head roofing nails spaced 6″ on center. Alternate stripping consists of 3″ wide 0.049″ diameter wire stripping weighing 1 pound per square yard and attached by No. 16 gage by 1½″ by ¾″ crown width staples, spaced 4″ on center. Plaster mixed 1:2 by weight, gypsum-to-sand aggregate. | — | — | — | 1 | — | — | — | ⅞
| 13-1.2 | Cement or gypsum plaster on metal lath. Lath fastened with 1½″ by No. 11 gage by ⁷⁄₁₆″ head barbed shank roofing nails spaced 5″ on center. Plaster mixed 1:2 for scratch coat and 1:3 for brown coat, by weight, cement to sand aggregate. | — | — | — | 1 | — | — | — | ⅝
| 13-1.3 | Perlite or vermiculite gypsum plaster on metal lath secured to joists with 1½″ by No. 11 gage by ⁷⁄₁₆″ head barbed shank roofing nails spaced 5″ on center. | — | — | — | 1 | — | — | — | ⅝
14. Plywood stressed skin panels consisting of ⅝″-thick interior C-D (exterior glue) top stressed skin on 2″ × 6″ nominal (minimum) stringers. Adjacent panel edges joined with 8d common wire nails spaced 6″ on center. Stringers spaced 12″ maximum on center. | 13-1.4 | ½″ Type X gypsum wallboardᶜ nailed to joists with 5d coolerᵒ or wallboardᵒ nails at 6″ on center. End joints of wallboard centered on joists. | — | — | — | 1 | — | — | — | ½
15. Vermiculite concrete slab proportioned 1:4 (portland cement to vermiculite aggregate) on a 1½″-deep steel deck supported on individually protected steel framing. Maximum span of deck 6″-10″ where deck is less than 0.019 inch (No. 26 carbon sheet steel gage) or greater. Slab reinforced with 4″× 8″ 0.109/0.083″ (No. 12/14 B.W. gage) welded wire mesh. | 14-1.1 | ½″-thick wood fiberboard weighing 15 to 18 pounds per cubic foot installed with long dimension parallel to stringers or ⅜″ C-D (exterior glue) plywood glued and/or nailed to stringers. Nailing to be with 5d coolerᵒ or wallboardᵒ nails at 12″ on center. Second layer of ½″ Type X gypsum wallboardᶜ applied with long dimension perpendicular to joists and attached with 8d coolerᵒ or wallboardᵒ nails at 6″ on center at end joints and 8″ on center elsewhere. Wallboard joints staggered with respect to fiberboard joints. | — | — | — | 1 | — | — | — | 1
16. Perlite concrete slab proportioned 1:6 (portland cement to perlite aggregate) on a 1¼″-deep steel deck supported on individually protected steel framing. Slab reinforced with 4″× 8″ 0.109/0.083″ (No… 12/14 B.W. gage) welded wire mesh. | 15-1.1 | None. | — | — | — | 3ʲ | — | — | — | —
17. Perlite concrete slab proportioned 1:6 (portland cement to perlite aggregate) on a ⁹⁄₁₆″-deep steel deck supported by steel joists 4’ on center. Class A or B roof covering on top. | 16-1.1 | None. | — | — | — | 3½ʲ | — | — | — | —
18. Perlite concrete slab proportioned 1:6 (portland cement to perlite aggregate) on 1¼″-deep steel deck supported on individually protected steel framing. Maximum span of deck 6’-10″ where deck is less than 0.019″(No. 26 carbon sheet steel gage) and 8’-0″ where deck is 0.019″(No. 26 carbon sheet steel gage) or greater. Slab reinforced with 0.042″ (No. 19 B.W. gage) hexagonal wire mesh. Class A or B roof covering on top. | 17-1.1 | Perlite gypsum plaster on metal lath wire tied to ¾″ furring channels attached with 0.065-inch (No. 16 B.W. gage) wire ties to lower chord of joists. | — | 2ᵖ | 2ᵖ | — | — | ⅞ | ¾ | —
19. Floor and beam construction consisting of 3″-deep cellular steel floor unit mounted on steel members with 1:4 (proportion of portland cement to perlite aggregate) perlite-concrete floor slab on top. | 18-1.1 | None. | — | 2¼ᵖ | 2¼ᵖ | — | — | — | — | —
20. Perlite concrete proportioned 1:6 (portland cement to perlite aggregate) poured to ⅜-inch thickness above top of corrugations of 1⁵⁄₁₆″-deep galvanized steel deck maximum span 8’-0″ for 0.024-inch (No. 24 galvanized sheet gage) or 6’ 0″ for 0.019-inch (No. 26 galvanized sheet gage) with deck supported by individually protected steel framing. Class A or B roof covering on top. | 19-1.1 | Suspended envelope ceiling of perlite gypsum plaster on metal lath attached to ¾″ cold-rolled channels, secured to 1½″ cold-rolled channels spaced 42″ on center supported by 0.203 inch (No. 6 B.W. gage) wire 36″ on center. Beams in envelope with 3″ minimum airspace between beam soffit and lath have a 4-hour rating. | 2ᵖ | — | — | — | 1ʲ | — | — | —
21. Wood joists, wood I-joists, floor trusses and flat or pitched roof trusses spaced a maximum 24″ o.c. with ½″ wood structural panels with exterior glue applied at right angles to top of joist or top chord of trusses with 8d nails. The wood structural panel thickness shall be not less than nominal ½″ nor less than required by Chapter 23. | 20-1.1 | None. | — | — | Varies | — | — | — | — | —
22. Steel joists, floor trusses and flat or pitched roof trusses spaced a maximum 24″ o.c. with ½″ wood structural panels with exterior glue applied at right angles to top of joist or top chord of trusses with No. 8 screws. The wood structural panel thickness shall be not less than nominal ½″ nor less than required by Chapter 23. | 21-1.1 | Base layer ⅝″ Type X gypsum wallboard applied at right angles to joist or truss 24″ o.c. with 1¼″ Type S or Type W drywall screws 24″ o.c. Face layer ⅝″ Type X gypsum wallboard or veneer base applied at right angles to joist or truss through base layer with 1⅞″ Type S or Type W drywall screws 12″ o.c. at joints and intermediate joist or truss. Face layer Type G drywall screws placed 2″ back on either side of face layer end joints, 12″ o.c. | — | — | — | Varies | — | — | — | 1¼
23. Wood I-joist (minimum joist depth 9¼″ with a minimum flange depth of 1⅝″ and a minimum flange cross-sectional area of 2.25 square inches) at 24″ o.c. spacing with a minimum 1″ × 4″ (¾″ × 3.5″ actual) ledger strip applied parallel to and covering the bottom of the bottom flange of each member, tacked in place. 2″ mineral wool insulation, 3.5 pcf (nominal) installed adjacent to the bottom flange of the I-joist and supported by the 1″ × 4″ ledger strip. | 22-1.1 | Base layer ⅝″ Type X gypsum board applied at right angles to steel framing 24″ on center with 1″ Type S drywall screws spaced 24″ on center. Face layer ⅝″ Type X gypsum board applied at right angles to steel framing attached through base layer with 1⅝″ Type S drywall screws 12″ on center at end joints and intermediate joints and 1½″ Type S drywall screws 12 inches on center placed 2″ back on either side of face layer end joints. Joints of the face layer are offset 24″ from the joints of the base layer. | — | — | — | Varies | — | — | — | 1¼
24. Wood I-joist (minimum I-joist depth 9¼″ with a minimum flange depth of 1½″ and a minimum flange cross-sectional area of 5.25 square inches; minimum web thickness of ⅜″) @ 24″ o.c., 1½″ mineral wool insulation (2.5 pcf — nominal) resting on hat-shaped furring channels. | 23-1.1 | ½″ deep single leg resilient channel 16″ on center (channels doubled at wallboard end joints), placed perpendicular to the furring strip and joist and attached to each joist by 1⅞″ Type S drywall screws. ⅝″ Type C gypsum wallboard applied perpendicular to the channel with end joints staggered not less than 4’ and fastened with 1⅜″ Type S drywall screws spaced 7″ on center. Wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | ⅝
25. Wood I-joist (minimum I-joist depth 9¼″ with a minimum flange depth of 1½″ and a minimum flange cross-sectional area of 5.25 square inches; minimum web thickness of ⁷⁄₁₆″) @ 24″ o.c., 1½″ mineral wool insulation (2.5 pcf — nominal) resting on resilient channels. | 24-1.1 | Minimum 0.026″ thick hat-shaped channel 16″ o.c. (channels doubled at wallboard end joints), placed perpendicular to the joist and attached to each joist by 1¼″ Type S drywall screws. ⅝″ Type C gypsum wallboard applied perpendicular to the channel with end joints staggered and fastened with 1⅜″ Type S drywall screws spaced 12″ o.c. in the field and 8″ o.c. at the wallboard ends. Wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | ⅝
26. Wood I-joist (minimum I-joist depth 9¼″ with a minimum flange thickness of 1½″ and a minimum flange cross-sectional area of 2.25 square inches; minimum web thickness of ⅜″) @ 24″ o.c. | 25-1.1 | Minimum 0.019″ thick resilient channel 16″ o.c. (channels doubled at wallboard end joints), placed perpendicular to the joist and attached to each joist by 1⅝″ Type S drywall screws. ⅝″ Type C gypsum wallboard applied perpendicular to the channel with end joints staggered and fastened with 1″ Type S drywall screws spaced 12″ o.c. in the field and 8″ o.c. at the wallboard ends. Wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | ⅝
27. Wood I-joist (minimum I-joist depth 9½″ with a minimum flange depth of 1⅝″ and a minimum flange cross-sectional area of 1.95 square inches; minimum web thickness of ⅜″) @ 24″ o.c. | 26-1.1 | Two layers of ½″ Type X gypsum wallboard applied with the long dimension perpendicular to the I-joists with end joints staggered. The base layer is fastened with 1⅝″ Type S drywall screws spaced 12″ o.c. and the face layer is fastened with 2″ Type S drywall screws spaced 12″ o.c. in the field and 8″ o.c. on the edges. Face layer end joints shall not occur on the same I-joist as base layer end joints and edge joints shall be offset 24″ from base layer joints. Face layer to also be attached to base layer with ½″ Type G drywall screws spaced 8″ o.c. placed 6″ from face layer end joints. Face layer wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | 1
28. Wood I-joist (minimum I-joist depth 9½″ with a minimum flange depth of 1½″ and a minimum flange cross-sectional area of 2.25 square inches; minimum web thickness of ⅜″) @ 24″ o.c. Unfaced fiberglass insulation or mineral wool insulation installed between the I-joists supported on the upper surface of the flange by stay wires spaced 12″ o.c. | 27-1.1 | Minimum 0.019″ thick resilient channel 16″ o.c. (channels doubled at wallboard end joints), placed perpendicular to the joist and attached to each joist by 1″ Type S drywall screws. Two layers of ½″ Type X gypsum wallboard applied with the long dimension perpendicular to the I-joists with end joints staggered. The base layer is fastened with 1¼″ Type S drywall screws 12″ o.c. and the face layer is fastened with 1″ Type S drywall screws spaced 12″ o.c. Face layer end joints shall not occur on the same I-joist as base layer end joints and edge joints shall be offset 24″ from base layer joints. Face layer to also be attached to base layer with ½″ Type G drywall screws spaced 8″ o.c. placed 6″ from face layer end joints. Face layer wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | 1
29. Channel-shaped 18 gage steel joists (minimum depth 8″) spaced a maximum 24″ o.c. supporting tongue-and-groove wood structural panels (nominal minimum ¾″ thick) applied perpendicular to framing members. Structural panels attached with 1⅝″ Type S-12 screws spaced 12″ o.c. | 28-1.1 | Base layer of ⅝″ Type C gypsum wallboard attached directly to I-joists with 1⅝″ Type S drywall screws 12″ o.c. with ends staggered. Minimum 0.0179″ thick hat-shaped ⅞-inch furring channel 16″ o.c. (channels doubled at wallboard end joints), placed perpendicular to the joist and attached to each joist by 1⅝″ Type S drywall screws after the base layer of gypsum wallboard has been applied. The middle and face layers of ⅝″ Type C gypsum wallboard applied perpendicular to the channel with end joints staggered. The middle is fastened with 1⅝″ Type S drywall screws spaced 12″ o.c. The face layer is applied parallel to the middle layer but with the edge joints offset 24″ from those of the middle layer and fastened with 1⅝″ Type S drywall screws 8″ o.c. The joints shall be taped and covered with joint compound. | — | — | — | Varies | — | — | 2¾ | —
30. Wood I-joist (minimum I-joist depth 9½″ with a minimum flange depth of 1½″ and a minimum flange cross-sectional area of 2.25 square inches, minimum web thickness of 3/8″) @ 24″ o.c. Fiberglass insulation placed between I-joist supported by the resilient channels. | 29-1.1 | Base layer ⅝″ Type X gypsum board applied perpendicular to bottom of framing members with 1⅜″ Type S-12 screws spaced 12″ o.c. Second layer ⅝″ Type X gypsum board attached perpendicular to framing members with 1⅝″ Type S-12 screws spaced 12″ o.c. Second layer joints offset 24″ from base layer. Third layer ⅝″ Type X gypsum board attached perpendicular to framing members with 2⅜″ Type S-12 screws spaced 12″ o.c. Third layer joints offset 12″ from second layer joints. Hat-shaped ⅞-inch rigid furring channels applied at right angles to framing members over third layer with two 2⅜″ Type S-12 screws at each framing member. Face layer ⅝″ Type X gypsum board applied at right angles to furring channels with 1⅜″ Type S screws spaced 12″ o.c. | — | — | Varies | — | — | — | 3⅜ | —
30. Wood I-joist (minimum I-joist depth 9½″ with a minimum flange depth of 1½″ and a minimum flange cross-sectional area of 2.25 square inches, minimum web thickness of ⅜″) @ 24″ o.c. Fiberglass insulation placed between I-joist supported by the resilient channels. | 30-1.1 | Minimum 0.019″ thick resilient channel 16″ o.c. (channels doubled at wallboard end joints), placed perpendicular to the joists and attached to each joist by 1¼″ Type S drywall screws. Two layers of ½″ Type X gypsum wallboard applied with the long dimension perpendicular to the I-joists with end joints staggered. The base layer is fastened with 1¼″ Type S drywall screws 12″ o.c. and the face layer is fastened with 1⅝″ Type S drywall screws spaced 12″ o.c. Face layer end joints shall not occur on the same I-joist as base layer end joints and edge joints shall be offset 24″ from base layer joints. Face layer to be attached to base layer with 1½″ Type G drywall screws spaced 8″ o.c. placed 6″ from face layer end joints. Face layer wallboard joints to be taped and covered with joint compound. | — | — | Varies | — | — | — | — | 1

## 722.2.1.1
TABLE 722.2.1.1
MINIMUM EQUIVALENT THICKNESS OF CAST-IN-PLACE OR PRECAST CONCRETE WALLS, LOAD BEARING OR NONLOAD-BEARING
CONCRETE TYPE | MINIMUM SLAB THICKNESS (inches) FOR FIRE-RESISTANCE RATING OF
| 1-hour | 1½ hours | 2 hours | 3 hours | 4 hours
Siliceous | 3.5 | 4.3 | 5 | 6.2 | 7
Carbonate | 3.2 | 4 | 4.6 | 5.7 | 6.6
Sand-lightweight | 2.7 | 3.3 | 3.8 | 4.6 | 5.4
Lightweight | 2.5 | 3.1 | 3.6 | 4.4 | 5.1

## 722.2.1.2(1)
TABLE 722.2.1.2(1)
VALUES OF Rⁿ°·⁵⁹ FOR USE IN EQUATION 7-4
TYPE OF MATERIAL | THICKNESS OF MATERIAL (inches)
| 1½ | 2 | 2½ | 3 | 3½ | 4 | 4½ | 5 | 5½ | 6 | 6½ | 7
Siliceous aggregate concrete | 5.3 | 6.5 | 8.1 | 9.5 | 11.3 | 13 | 14.9 | 16.9 | 18.8 | 20.7 | 22.8 | 25.1
Carbonate aggregate concrete | 5.5 | 7.1 | 8.9 | 10.4 | 12 | 14 | 16.2 | 18.1 | 20.3 | 21.9 | 24.7 | 27.2ᶜ
Sand-lightweight concrete | 6.5 | 8.2 | 10.5 | 12.8 | 15.5 | 18.1 | 20.7 | 23.3 | 26.0ᶜ | Note c | Note c | Note c
Lightweight concrete | 6.6 | 8.8 | 11.2 | 13.7 | 16.5 | 19.1 | 21.9 | 24.7 | 27.8ᶜ | Note c | Note c | Note c
Insulating concreteᵃ | 9.3 | 13.3 | 16.6 | 18.3 | 23.1 | 26.5ᶜ | Note c | Note c | Note c | Note c | Note c | Note c
Airspaceᵇ | — | — | — | — | — | — | — | — | — | — | — | —

## 722.2.1.2(2)
TABLE 722.2.1.2(2)
FIRE-RESISTANCE RATINGS BASED ON R°·⁵⁹
R ᵃ, MINUTES | R °·⁵⁹
60 | 11.2
120 | 16.85
180 | 21.41
240 | 25.37

## 722.2.1.4(1)
TABLE 722.2.1.4(1)
MULTIPLYING FACTOR FOR FINISHES ON NONFIRE-EXPOSED SIDE OF WALL
TYPE OF FINISH APPLIED TO CONCRETE OR CONCRETE MASONRY WALL | TYPE OF AGGREGATE USED IN CONCRETE OR CONCRETE MASONRY
| Concrete: siliceous or carbonate Concrete Masonry: siliceous or carbonate; solid clay brick | Concrete: sand-lightweight Concrete Masonry: clay tile; hollow clay brick; concrete masonry units of expanded shale and < 20% sand | Concrete: lightweight Concrete Masonry: concrete masonry units of expanded shale, expanded clay, expanded slag, or pumice < 20% sand | Concrete Masonry: concrete masonry units of expanded slag, expanded clay, or pumice
Portland cement-sand plaster | 1 | 0.75ᵃ | 0.75ᵃ | 0.50ᵃ
Gypsum-sand plaster | 1.25 | 1 | 1 | 1
Gypsum-vermiculite or perlite plaster | 1.75 | 1.5 | 1.25 | 1.25
Gypsum wallboard | 3 | 2.25 | 2.25 | 2.25

## 722.2.1.4(2)
TABLE 722.2.1.4(2)
TIME ASSIGNED TO FINISH MATERIALS ON FIRE-EXPOSED SIDE OF WALL
FINISH DESCRIPTION | TIME (minute)
Gypsum wallboard ⅜ inch | 10
½ inch | 15
⅝ inch | 20
2 layers of ⅜ inch | 25
1 layer of ⅜ inch, 1 layer of ½ inch | 35
2 layers of ½ inch | 40
Type X gypsum wallboard ½ inch | 25
⅝ inch | 40
Portland cement-sand plaster applied directly to concrete masonry | See Note a
Portland cement-sand plaster on metal lath ¾ inch | 20
⅞ inch | 25
1 inch | 30
Gypsum sand plaster on ⅜-inch gypsum lath ½ inch | 35
⅝ inch | 40
¾ inch | 50
Gypsum sand plaster on metal lath ¾ inch | 50
⅞ inch | 60
1 inch | 80

## 722.2.2.1
TABLE 722.2.2.1
MINIMUM SLAB THICKNESS (inches)
CONCRETE TYPE | FIRE-RESISTANCE RATING (hours)
| 1 | 1½ | 2 | 3 | 4
Siliceous | 3.5 | 4.3 | 5 | 6.2 | 7
Carbonate | 3.2 | 4 | 4.6 | 5.7 | 6.6
Sand-lightweight | 2.7 | 3.3 | 3.8 | 4.6 | 5.4
Lightweight | 2.5 | 3.1 | 3.6 | 4.4 | 5.1

## 722.2.3(1)
TABLE 722.2.3(1)
COVER THICKNESS FOR REINFORCED CONCRETE FLOOR OR ROOF SLABS (inches)
CONCRETE AGGREGATE TYPE | FIRE-RESISTANCE RATING (hours)
| Restrained |  |  |  |  | Unrestrained
| 1 | 1½ | 2 | 3 | 4 | 1 | 1½ | 2 | 3 | 4
Siliceous | ¾ | ¾ | ¾ | ¾ | ¾ | ¾ | ¾ | 1 | 1¼ | 1⅝
Carbonate | ¾ | ¾ | ¾ | ¾ | ¾ | ¾ | ¾ | ¾ | 1¼ | 1¼
Sand-lightweight or lightweight | ¾ | ¾ | ¾ | ¾ | ¾ | ¾ | ¾ | ¾ | 1¼ | 1¼
For SI: 1 inch = 25.4 mm.

## 722.2.3(2)
TABLE 722.2.3(2)
COVER THICKNESS FOR PRESTRESSED CONCRETE FLOOR OR ROOF SLABS (inches)
CONCRETE AGGREGATE TYPE | FIRE-RESISTANCE RATING (hours)
| Restrained |  |  |  |  | Unrestrained
| 1 | 1½ | 2 | 3 | 4 | 1 | 1½ | 2 | 3 | 4
Siliceous | ¾ | ¾ | ¾ | ¾ | ¾ | 1⅜ | 1½ | 1¾ | 2⅜ | 2¼
Carbonate | ¾ | ¾ | ¾ | ¾ | ¾ | 1 | 1⅜ | 1⅝ | 2⅜ | 2¼
Sand-lightweight or lightweight | ¾ | ¾ | ¾ | ¾ | ¾ | 1 | 1⅜ | 1½ | 2 | 2¼
For SI: 1 inch = 25.4 mm.

## 722.2.3(3)
TABLE 722.2.3(3)
MINIMUM COVER FOR MAIN REINFORCING BARS OF REINFORCED CONCRETE BEAMSᶜ (APPLICABLE TO ALL TYPES OF STRUCTURAL CONCRETE)
RESTRAINED OR UNRESTRAINEDᵃ | BEAM WIDTHᵇ (inches) | FIRE-RESISTANCE RATING (hours)
|  | 1 | 1½ | 2 | 3 | 4
Restrained | 5 | ¾ | ¾ | ¾ | 1ᵃ | 1¼ᵃ
| 7 | ¾ | ¾ | ¾ | ¾ | ¾
| ≥ 10 | ¾ | ¾ | ¾ | ¾ | ¾
Unrestrained | 5 | ¾ | 1 | 1¼ | — | —
| 7 | ¾ | ¾ | ¾ | 1¾ | 3
| ≥ 10 | ¾ | ¾ | 1 | 1¾ | 1¾

## 722.2.3(4)
TABLE 722.2.3(4)
MINIMUM COVER FOR PRESTRESSED CONCRETE BEAMS 8 INCHES OR GREATER IN WIDTHᵇ
RESTRAINED OR UNRESTRAINEDᵃ | CONCRETE AGGREGATE TYPE | BEAM WIDTHᵇ (inches) | FIRE-RESISTANCE RATING (hours)
|  |  | 1 | 1½ | 2 | 3 | 4
Restrained | Carbonate or siliceous | 8 | 1½ | 1½ | 1½ | 1¾ᵃ | 2½ᵃ
| Carbonate or siliceous | ≥ 12 | 1½ | 1½ | 1½ | 1½ | 1⅞ᵃ
| Sand lightweight | 8 | 1½ | 1½ | 1½ | 1½ | 2ᵃ
| Sand lightweight | ≥ 12 | 1½ | 1½ | 1½ | 1½ | 1⅝ᵃ
Unrestrained | Carbonate or siliceous | 8 | 1½ | 1¾ | 2½ | 5ᶜ | —
| Carbonate or siliceous | ≥ 12 | 1½ | 1½ | 1⅞ᵃ | 2½ | 3
| Sand lightweight | 8 | 1½ | 1½ | 2 | 3¾ | —
| Sand lightweight | ≥ 12 | 1½ | 1½ | 1⅝ | 2 | 2½

## 722.2.3(5)
TABLE 722.2.3(5)
MINIMUM COVER FOR PRESTRESSED CONCRETE BEAMS OF ALL WIDTHS
RESTRAINED OR UNRESTRAINEDᵃ | CONCRETE AGGREGATE TYPE | BEAM AREAᵇ A (square inches) | FIRE-RESISTANCE RATING (hours)
|  |  | 1 | 1½ | 2 | 3 | 4
Restrained | All | 40 ≤ A ≤ 150 | 1½ | 1½ | 2 | 2½ | —
| Carbonate or siliceous | 150 < A ≤ 300 | 1½ | 1½ | 1½ | 1¾ | 2½
|  | 300 < A | 1½ | 1½ | 1½ | 1½ | 2
| Sand lightweight | 150 < A | 1½ | 1½ | 1½ | 1½ | 2
Unrestrained | All | 40 ≤ A ≤ 150 | 2 | 2½ | — | — | —
| Carbonate or siliceous | 150 < A ≤ 300 | 1½ | 1¾ | 2½ | — | —
|  | 300 < A | 1½ | 1½ | 2 | 3ᶜ | 4ᶜ
| Sand lightweight | 150 < A | 1½ | 1½ | 2 | 3ᶜ | 4ᶜ

## 722.2.4
TABLE 722.2.4
MINIMUM DIMENSION OF CONCRETE COLUMNS (inches)
TYPES OF CONCRETE | FIRE-RESISTANCE RATING (hours)
| 1 | 1½ | 2ᵃ | 3ᵃ | 4ᵇ
Siliceous | 8 | 9 | 10 | 12 | 14
Carbonate | 8 | 9 | 10 | 11 | 12
Sand-lightweight | 8 | 8½ | 9 | 10½ | 12

## 722.3.2
TABLE 722.3.2
MINIMUM EQUIVALENT THICKNESS (inches) OF BEARING OR NONBEARING CONCRETE MASONRY WALLSᵃ, ᵇ, ᶜ, ᵈ
TYPE OF AGGREGATE | FIRE-RESISTANCE RATING (hours)
| ½ | ¾ | 1 | 1¼ | 1½ | 1¾ | 2 | 2¼ | 2½ | 2¾ | 3 | 3¼ | 3½ | 3¾ | 4
Pumice or expanded slag | 1.5 | 1.9 | 2.1 | 2.5 | 2.7 | 3 | 3.2 | 3.4 | 3.6 | 3.8 | 4 | 4.2 | 4.4 | 4.5 | 4.7
Expanded shale, clay or slate | 1.8 | 2.2 | 2.6 | 2.9 | 3.3 | 3.4 | 3.6 | 3.8 | 4 | 4.2 | 4.4 | 4.6 | 4.8 | 4.9 | 5.1
Limestone, cinders or unexpanded slag | 1.9 | 2.3 | 2.7 | 3.1 | 3.4 | 3.7 | 4 | 4.3 | 4.5 | 4.8 | 5 | 5.2 | 5.5 | 5.7 | 5.9
Calcareous or siliceous gravel | 2 | 2.4 | 2.8 | 3.2 | 3.6 | 3.9 | 4.2 | 4.5 | 4.8 | 5 | 5.3 | 5.5 | 5.8 | 6 | 6.2

## 722.3.4
TABLE 722.3.4
MINIMUM COVER OF LONGITUDINAL REINFORCEMENT IN FIRE-RESISTANCE-RATED REINFORCED CONCRETE MASONRY LINTELS (inches)
NOMINAL WIDTH OF LINTEL (inches) | FIRE-RESISTANCE RATING (hours)
| 1 | 2 | 3 | 4
6 | 1½ | 2 | — | —
8 | 1½ | 1½ | 1¾ | 3
10 or greater | 1½ | 1½ | 1½ | 1¾
For SI: 1 inch = 25.4 mm.

## 722.3.5
TABLE 722.3.5
MINIMUM DIMENSION OF CONCRETE MASONRY COLUMNS (inches)
FIRE-RESISTANCE RATING (hours)
1 | 2 | 3 | 4
8 inches | 10 inches | 12 inches | 14 inches

## 722.4.1(1)
TABLE 722.4.1(1)
FIRE-RESISTANCE PERIODS OF CLAY MASONRY WALLS
MATERIAL TYPE | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE RESISTANCEᵃ, ᵇ, ᶜ (inches)
| 1 hour | 2 hours | 3 hours | 4 hours
Solid brick of clay or shaleᵈ | 2.7 | 3.8 | 4.9 | 6
Hollow brick or tile of clay or shale, unfilled | 2.3 | 3.4 | 4.3 | 5
Hollow brick or tile of clay or shale, grouted or filled with materials specified in Section 722.4.1.1.3 | 3 | 4.4 | 5.5 | 6.6

## 722.4.1(2)
TABLE 722.4.1(2)
FIRE-RESISTANCE RATINGS FOR BEARING STEEL FRAME BRICK VENEER WALLS OR PARTITIONS
WALL OR PARTITION ASSEMBLY | PLASTER SIDE EXPOSED (hours) | BRICK FACED SIDE EXPOSED (hours)
Outside facing of steel studs: ½″ wood fiberboard sheathing next to studs, ⅜″ airspace formed with ¾″ × 1⅝″ wood strips placed over the fiberboard and secured to the studs; metal or wire lath nailed to such strips, ¾″ brick veneer held in place by filling ¾″ airspace between the back of brick and studs with mortar. Inside facing of studs: ¾″ unsanded gypsum plaster on metal or wire lath attached to ⅝″ wood strips secured to edges of the studs. | 1.5 | 4
Outside facing of steel studs: 1″ insulation board sheathing attached to studs, 1″ airspace, and 3¾″ brick veneer attached to steel frame with metal ties every 5th course. Inside facing of studs: ⅞″ sanded gypsum plaster (1:2 mix) applied on metal or wire lath attached directly to the studs. | 1.5 | 4
Same as above except use ⅞″ vermiculite—gypsum plaster or 1″ sanded gypsum plaster (1:2 mix) applied to metal or wire. | 2 | 4
Outside facing of steel studs: ½″ gypsum sheathing board, attached to studs, and 3¾″ brick veneer attached to steel frame with metal ties every 5th course. Inside facing of studs: ½″ sanded gypsum plaster (1:2 mix) applied to ½″ perforated gypsum lath securely attached to studs and having strips of metal lath 3 inches wide applied to all horizontal joints of gypsum lath. | 2 | 4

## 722.4.1(3)
TABLE 722.4.1(3)
VALUES OF Rⁿ°·⁵⁹
Rⁿ°·⁵⁹ | R (hours)
1 | 1
2 | 1.5
3 | 1.91
4 | 2.27

## 722.4.1(4)
TABLE 722.4.1(4)
COEFFICIENTS FOR PLASTER, plᵇ
THICKNESS OF PLASTER (inch) | ONE SIDE | TWO SIDES
½ inch | 0.3 | 0.6
⅝ inch | 0.37 | 0.75
¾ inch | 0.45 | 0.9

## 722.4.1(5)
TABLE 722.4.1(5)
REINFORCED MASONRY LINTELS
NOMINAL LINTEL WIDTH (inches) | MINIMUM LONGITUDINAL REINFORCEMENT COVER FOR FIRE RESISTANCE (inches)
| 1 hour | 2 hours | 3 hours | 4 hours
6 | 1½ | 2 | NP | NP
8 | 1½ | 1½ | 1¾ | 3
10 or more | 1½ | 1½ | 1½ | 1¾

## 722.4.1(6)
TABLE 722.4.1(6)
REINFORCED CLAY MASONRY COLUMNS
COLUMN SIZE | FIRE-RESISTANCE RATING (hours)
| 1 | 2 | 3 | 4
Minimum column dimension (inches) | 8 | 10 | 12 | 14

## 722.5.1(1)
TABLE 722.5.1(1)
W/D RATIOS FOR STEEL COLUMNS
STRUCTURAL SHAPE | CONTOUR PROFILE | BOX PROFILE | STRUCTURAL SHAPE | CONTOUR PROFILE | BOX PROFILE
W14 × 233 | 2.55 | 3.65 | W10 × 112 | 1.81 | 2.57
× 211 | 2.32 | 3.35 | × 100 | 1.64 | 2.33
× 193 | 2.14 | 3.09 | × 88 | 1.45 | 2.08
× 176 | 1.96 | 2.85 | × 77 | 1.28 | 1.85
× 159 | 1.78 | 2.6 | × 68 | 1.15 | 1.66
× 145 | 1.64 | 2.39 | × 60 | 1.01 | 1.48
× 132 | 1.56 | 2.25 | × 54 | 0.922 | 1.34
× 120 | 1.42 | 2.06 | × 49 | 0.84 | 1.23
× 109 | 1.29 | 1.88 | × 45 | 0.888 | 1.24
× 99 | 1.18 | 1.72 | × 39 | 0.78 | 1.09
× 90 | 1.08 | 1.58 | × 33 | 0.661 | 0.93
× 82 | 1.23 | 1.68
× 74 | 1.12 | 1.53 | W8 × 67 | 1.37 | 1.94
× 68 | 1.04 | 1.41 | × 58 | 1.2 | 1.71
× 61 | 0.928 | 1.28 | × 48 | 1 | 1.44
× 53 | 0.915 | 1.21 | × 40 | 0.849 | 1.23
× 48 | 0.835 | 1.1 | × 35 | 0.749 | 1.08
× 43 | 0.752 | 0.99 | × 31 | 0.665 | 0.97
|  |  | × 28 | 0.688 | 0.96
W12 × 190 | 2.5 | 3.51 | × 24 | 0.591 | 0.83
× 170 | 2.26 | 3.2 | × 21 | 0.577 | 0.77
× 152 | 2.04 | 2.9 | × 18 | 0.499 | 0.67
× 136 | 1.86 | 2.63
× 120 | 1.65 | 2.36 | W6 × 25 | 0.696 | 1
× 106 | 1.47 | 2.11 | × 20 | 0.563 | 0.82
× 96 | 1.34 | 1.93 | × 16 | 0.583 | 0.78
× 87 | 1.22 | 1.76 | × 15 | 0.431 | 0.63
× 79 | 1.11 | 1.61 | × 12 | 0.448 | 0.6
× 72 | 1.02 | 1.48 | × 9 | 0.338 | 0.46
× 65 | 0.925 | 1.35
× 58 | 0.925 | 1.31 | W5 × 19 | 0.644 | 0.93
× 53 | 0.855 | 1.2 | × 16 | 0.55 | 0.8
× 50 | 0.909 | 1.23
× 45 | 0.829 | 1.12 | W4 × 13 | 0.556 | 0.79
× 40 | 0.734 | 1

## 722.5.1(2)
TABLE 722.5.1(2)
PROPERTIES OF CONCRETE
PROPERTY | NORMAL WEIGHT CONCRETE | STRUCTURAL LIGHTWEIGHT CONCRETE
Thermal conductivity (kᶜ) | 0.95 Btu/hr • ft • °F | 0.35 Btu/hr • ft • °F
Specific heat (cᶜ) | 0.20 Btu/lb °F | 0.20 Btu/lb °F
Density (Pᶜ) | 145 lb/ft³ | 110 lb/ft³
Equilibrium (free) moisture content (m) by volume | 4% | 5%

## 722.5.1(3)
TABLE 722.5.1(3)
THERMAL CONDUCTIVITY OF CONCRETE OR CLAY MASONRY UNITS
DENSITY (dₘ) OF UNITS (lb/ft³) | THERMAL CONDUCTIVITY (K) OF UNITS (Btu/hr • ft • °F)
Concrete Masonry Units
80 | 0.207
85 | 0.228
90 | 0.252
95 | 0.278
100 | 0.308
105 | 0.34
110 | 0.376
115 | 0.416
120 | 0.459
125 | 0.508
130 | 0.561
135 | 0.62
140 | 0.685
145 | 0.758
150 | 0.837
Clay Masonry Units
120 | 1.25
130 | 2.25

## 722.5.1(4)
TABLE 722.5.1(4)
WEIGHT-TO-HEATED-PERIMETER RATIOS (W/D) FOR TYPICAL WIDE FLANGE BEAM AND GIRDER SHAPES
STRUCTURAL SHAPE | CONTOUR PROFILE | BOX PROFILE | STRUCTURAL SHAPE | CONTOUR PROFILE | BOX PROFILE
W36 × 300 | 2.5 | 3.33 | W24 × 68 | 0.942 | 1.21
× 280 | 2.35 | 3.12 | × 62 | 0.934 | 1.14
× 260 | 2.18 | 2.92 | × 55 | 0.828 | 1.02
× 245 | 2.08 | 2.76
× 230 | 1.95 | 2.61 | W21 × 147 | 1.87 | 2.6
× 210 | 1.96 | 2.45 | × 132 | 1.68 | 2.35
× 194 | 1.81 | 2.28 | × 122 | 1.57 | 2.19
× 182 | 1.72 | 2.15 | × 111 | 1.43 | 2.01
× 170 | 1.6 | 2.01 | × 101 | 1.3 | 1.84
× 160 | 1.51 | 1.9 | × 93 | 1.4 | 1.8
× 150 | 1.43 | 1.79 | × 83 | 1.26 | 1.62
× 135 | 1.29 | 1.63 | × 73 | 1.11 | 1.44
|  |  | × 68 | 1.04 | 1.35
W33 × 241 | 2.13 | 2.86 | W21 × 62 | 0.952 | 1.23
× 221 | 1.97 | 2.64 | × 57 | 0.952 | 1.17
× 201 | 1.79 | 2.42 | × 50 | 0.838 | 1.04
× 152 | 1.53 | 1.94 | × 44 | 0.746 | 0.92
× 141 | 1.43 | 1.8
× 130 | 1.32 | 1.67 | W18 × 119 | 1.72 | 2.42
× 118 | 1.21 | 1.53 | × 106 | 1.55 | 2.18
|  |  | × 97 | 1.42 | 2.01
W30 × 211 | 2.01 | 2.74 | × 86 | 1.27 | 1.8
× 191 | 1.85 | 2.5 | × 76 | 1.13 | 1.6
× 173 | 1.66 | 2.28 | × 71 | 1.22 | 1.59
× 132 | 1.47 | 1.85 | × 65 | 1.13 | 1.47
× 124 | 1.39 | 1.75 | × 60 | 1.04 | 1.36
× 116 | 1.3 | 1.65 | × 55 | 0.963 | 1.26
× 108 | 1.21 | 1.54 | × 50 | 0.88 | 1.15
× 99 | 1.12 | 1.42 | × 46 | 0.878 | 1.09
|  |  | × 40 | 0.768 | 0.96
W27 × 178 | 1.87 | 2.55 | × 35 | 0.672 | 0.85
× 161 | 1.7 | 2.33
× 146 | 1.55 | 2.12 | W16 × 100 | 1.59 | 2.25
× 114 | 1.39 | 1.76 | × 89 | 1.43 | 2.03
× 102 | 1.24 | 1.59 | × 77 | 1.25 | 1.78
× 94 | 1.15 | 1.47 | × 67 | 1.09 | 1.56
× 84 | 1.03 | 1.33 | × 57 | 1.09 | 1.43
|  |  | × 50 | 0.962 | 1.26
|  |  | × 45 | 0.87 | 1.15
W24 × 162 | 1.88 | 2.57 | × 40 | 0.78 | 1.03
× 146 | 1.7 | 2.34 | × 36 | 0.702 | 0.93
× 131 | 1.54 | 2.12 | × 31 | 0.661 | 0.83
× 117 | 1.38 | 1.91 | × 26 | 0.558 | 0.7
× 104 | 1.24 | 1.71
× 94 | 1.28 | 1.63 | W14 × 132 | 1.89 | 3
□ 84 | 1.15 | 1.47 | × 120 | 1.71 | 2.75
× 76 | 1.05 | 1.34 | × 109 | 1.57 | 2.52
W14 × 99 | 1.43 | 2.31 | W10 × 30 | 0.806 | 1.12
× 90 | 1.31 | 2.11 | × 26 | 1.708 | 0.98
× 82 | 1.45 | 2.12 | × 22 | 0.606 | 0.84
× 74 | 1.32 | 1.93 | × 19 | 0.607 | 0.78
× 68 | 1.22 | 1.78 | × 17 | 0.543 | 0.7
× 61 | 1.1 | 1.61 | × 15 | 0.484 | 0.63
× 53 | 1.06 | 1.48 | × 12 | 0.392 | 0.51
× 48 | 0.97 | 1.35
W14 × 43 | 0.874 | 1.22 | W8 × 67 | 1.65 | 2.55
× 38 | 0.809 | 1.09 | × 58 | 1.44 | 2.26
× 34 | 0.725 | 0.98 | × 48 | 1.21 | 1.91
× 30 | 0.644 | 0.87 | × 40 | 1.03 | 1.63
× 26 | 0.628 | 0.79 | × 35 | 0.907 | 1.44
× 22 | 0.534 | 0.68 | × 31 | 0.803 | 1.29
|  |  | × 28 | 0.819 | 1.24
W12 × 87 | 1.47 | 2.34 | × 24 | 0.704 | 1.07
× 79 | 1.34 | 2.14 | × 21 | 0.675 | 0.96
× 72 | 1.23 | 1.97 | × 18 | 0.583 | 0.84
× 65 | 1.11 | 1.79 | × 15 | 0.551 | 0.74
× 58 | 1.1 | 1.69 | × 13 | 0.483 | 0.65
× 53 | 1.02 | 1.55 | × 10 | 0.375 | 0.51
× 50 | 1.06 | 1.54
× 45 | 0.974 | 1.4 | W6 × 25 | 0.839 | 1.33
× 40 | 0.86 | 1.25 | × 20 | 0.678 | 1.09
× 35 | 0.81 | 1.11 | × 16 | 0.684 | 0.96
× 30 | 0.699 | 0.96 | × 15 | 0.521 | 0.83
× 26 | 0.612 | 0.84 | × 12 | 0.526 | 0.75
× 22 | 0.623 | 0.77 | × 9 | 0.398 | 0.57
× 19 | 0.54 | 0.67
× 16 | 0.457 | 0.57 | W5 × 19 | 0.776 | 1.24
× 14 | 0.405 | 0.5 | × 16 | 0.664 | 1.07
W10 × 112 | 2.17 | 3.38 | W4 × 13 | 0.67 | 1.05
× 100 | 1.97 | 3.07
× 88 | 1.74 | 2.75
× 77 | 1.54 | 2.45
× 68 | 1.38 | 2.2
× 60 | 1.22 | 1.97
× 54 | 1.11 | 1.79
× 49 | 1.01 | 1.64
× 45 | 1.06 | 1.59
× 39 | 0.94 | 1.4
× 33 | 0.77 | 1.2

## 722.5.1(5)
TABLE 722.5.1(5)
FIRE RESISTANCE OF CONCRETE MASONRY PROTECTED STEEL COLUMNS
COLUMN SIZE | CONCRETE MASONRY DENSITY POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CONCRETE MASONRY PROTECTION ASSEMBLY, Tₒ (inches) |  |  |  | COLUMN SIZE | CONCRETE MASONRY DENSITY POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS RATING OF CONCRETE MASONRY PROTECTION ASSEMBLY, Tₒ (inches)
|  | 1 hour | 2 hours | 3 hours | 4 hours |  |  | 1 hour | 2 hours | 3 hours | 4 hours
W14 × 82 | 80 | 0.74 | 1.61 | 2.36 | 3.04 | W10 × 68 | 80 | 0.72 | 1.58 | 2.33 | 3.01
| 100 | 0.89 | 1.85 | 2.67 | 3.4 |  | 100 | 0.87 | 1.83 | 2.65 | 3.38
| 110 | 0.96 | 1.97 | 2.81 | 3.57 |  | 110 | 0.94 | 1.95 | 2.79 | 3.55
| 120 | 1.03 | 2.08 | 2.95 | 3.73 |  | 120 | 1.01 | 2.06 | 2.94 | 3.72
W14 × 68 | 80 | 0.83 | 1.7 | 2.45 | 3.13 | W10 × 54 | 80 | 0.88 | 1.76 | 2.53 | 3.21
| 100 | 0.99 | 1.95 | 2.76 | 3.49 |  | 100 | 1.04 | 2.01 | 2.83 | 3.57
| 110 | 1.06 | 2.06 | 2.91 | 3.66 |  | 110 | 1.11 | 2.12 | 2.98 | 3.73
| 120 | 1.14 | 2.18 | 3.05 | 3.82 |  | 120 | 1.19 | 2.24 | 3.12 | 3.9
W14 × 53 | 80 | 0.91 | 1.81 | 2.58 | 3.27 | W10 × 45 | 80 | 0.92 | 1.83 | 2.6 | 3.3
| 100 | 1.07 | 2.05 | 2.88 | 3.62 |  | 100 | 1.08 | 2.07 | 2.9 | 3.64
| 110 | 1.15 | 2.17 | 3.02 | 3.78 |  | 110 | 1.16 | 2.18 | 3.04 | 3.8
| 120 | 1.22 | 2.28 | 3.16 | 3.94 |  | 120 | 1.23 | 2.29 | 3.18 | 3.96
W14 × 43 | 80 | 1.01 | 1.93 | 2.71 | 3.41 | W10 × 33 | 80 | 1.06 | 2 | 2.79 | 3.49
| 100 | 1.17 | 2.17 | 3 | 3.74 |  | 100 | 1.22 | 2.23 | 3.07 | 3.81
| 110 | 1.25 | 2.28 | 3.14 | 3.9 |  | 110 | 1.3 | 2.34 | 3.2 | 3.96
| 120 | 1.32 | 2.38 | 3.27 | 4.05 |  | 120 | 1.37 | 2.44 | 3.33 | 4.12
W12 × 72 | 80 | 0.81 | 1.66 | 2.41 | 3.09 | W8 × 40 | 80 | 0.94 | 1.85 | 2.63 | 3.33
| 100 | 0.91 | 1.88 | 2.7 | 3.43 |  | 100 | 1.1 | 2.1 | 2.93 | 3.67
| 110 | 0.99 | 1.99 | 2.84 | 3.6 |  | 110 | 1.18 | 2.21 | 3.07 | 3.83
| 120 | 1.06 | 2.1 | 2.98 | 3.76 |  | 120 | 1.25 | 2.32 | 3.2 | 3.99
W12 × 58 | 80 | 0.88 | 1.76 | 2.52 | 3.21 | W8 × 31 | 80 | 1.06 | 2 | 2.78 | 3.49
| 100 | 1.04 | 2.01 | 2.83 | 3.56 |  | 100 | 1.22 | 2.23 | 3.07 | 3.81
| 110 | 1.11 | 2.12 | 2.97 | 3.73 |  | 110 | 1.29 | 2.33 | 3.2 | 3.97
| 120 | 1.19 | 2.23 | 3.11 | 3.89 |  | 120 | 1.36 | 2.44 | 3.33 | 4.12
W12 × 50 | 80 | 0.91 | 1.81 | 2.58 | 3.27 | W8 × 24 | 80 | 1.14 | 2.09 | 2.89 | 3.59
| 100 | 1.07 | 2.05 | 2.88 | 3.62 |  | 100 | 1.29 | 2.31 | 3.16 | 3.9
| 110 | 1.15 | 2.17 | 3.02 | 3.78 |  | 110 | 1.36 | 2.42 | 3.28 | 4.05
| 120 | 1.22 | 2.28 | 3.16 | 3.94 |  | 120 | 1.43 | 2.52 | 3.41 | 4.2
W12 × 40 | 80 | 1.01 | 1.94 | 2.72 | 3.41 | W8 × 18 | 80‡ | 1.22 | 2.2 | 3.01 | 3.72
| 100 | 1.17 | 2.17 | 3.01 | 3.75 |  | 100 | 1.36 | 2.4 | 3.25 | 4.01
| 110 | 1.25 | 2.28 | 3.14 | 3.9 |  | 110 | 1.42 | 2.5 | 3.37 | 4.14
| 120 | 1.32 | 2.39 | 3.27 | 4.06 |  | 120 | 1.48 | 2.59 | 3.49 | 4.28
4 × 4 × ½ wall thickness | 80 | 0.93 | 1.9 | 2.71 | 3.43 | 4 double extra strong 0.674 wall thickness | 80 | 0.8 | 1.75 | 2.56 | 3.28
| 100 | 1.08 | 2.13 | 2.99 | 3.76 |  | 100 | 0.95 | 1.99 | 2.85 | 3.62
| 110 | 1.16 | 2.24 | 3.13 | 3.91 |  | 110 | 1.02 | 2.1 | 2.99 | 3.78
| 120 | 1.22 | 2.34 | 3.26 | 4.06 |  | 120 | 1.09 | 2.2 | 3.12 | 3.93
4 × 4 × ⅜ wall thickness | 80 | 1.05 | 2.03 | 2.84 | 3.57 | 4 extra strong 0.337 wall thickness | 80 | 1.12 | 2.11 | 2.93 | 3.65
| 100 | 1.2 | 2.25 | 3.11 | 3.88 |  | 100 | 1.26 | 2.32 | 3.19 | 3.95
| 110 | 1.27 | 2.35 | 3.24 | 4.02 |  | 110 | 1.33 | 2.42 | 3.31 | 4.09
| 120 | 1.34 | 2.45 | 3.37 | 4.17 |  | 120 | 1.4 | 2.52 | 3.43 | 4.23
4 × 4 × ¼ wall thickness | 80 | 1.21 | 2.2 | 3.01 | 3.73 | 4 standard 0.237 wall thickness | 80 | 1.26 | 2.25 | 3.07 | 3.79
| 100 | 1.35 | 2.4 | 3.26 | 4.02 |  | 100 | 1.4 | 2.45 | 3.31 | 4.07
| 110 | 1.41 | 2.5 | 3.38 | 4.16 |  | 110 | 1.46 | 2.55 | 3.43 | 4.21
| 120 | 1.48 | 2.59 | 3.5 | 4.3 |  | 120 | 1.53 | 2.64 | 3.54 | 4.34
6 × 6 × ½ wall thickness | 80 | 0.82 | 1.75 | 2.54 | 3.25 | 5 double extra strong 0.750 wall thickness | 80 | 0.7 | 1.61 | 2.4 | 3.12
| 100 | 0.98 | 1.99 | 2.84 | 3.59 |  | 100 | 0.85 | 1.86 | 2.71 | 3.47
| 110 | 1.05 | 2.1 | 2.98 | 3.75 |  | 110 | 0.91 | 1.97 | 2.85 | 3.63
| 120 | 1.12 | 2.21 | 3.11 | 3.91 |  | 120 | 0.98 | 2.02 | 2.99 | 3.79
6 × 6 × ⅜ wall thickness | 80 | 0.96 | 1.91 | 2.71 | 3.42 | 5 extra strong 0.375 wall thickness | 80 | 1.04 | 2.01 | 2.83 | 3.54
| 100 | 1.12 | 2.14 | 3 | 3.75 |  | 100 | 1.19 | 2.23 | 3.09 | 3.85
| 110 | 1.19 | 2.25 | 3.13 | 3.9 |  | 110 | 1.26 | 2.34 | 3.22 | 4
| 120 | 1.26 | 2.35 | 3.26 | 4.05 |  | 120 | 1.32 | 2.44 | 3.34 | 4.14
6 × 6 × ¼ wall thickness | 80 | 1.14 | 2.11 | 2.92 | 3.63 | 5 standard 0.258 wall thickness | 80 | 1.2 | 2.19 | 3 | 3.72
| 100 | 1.29 | 2.32 | 3.18 | 3.93 |  | 100 | 1.34 | 2.39 | 3.25 | 4
| 110 | 1.36 | 2.43 | 3.3 | 4.08 |  | 110 | 1.41 | 2.49 | 3.37 | 4.14
| 120 | 1.42 | 2.52 | 3.43 | 4.22 |  | 120 | 1.47 | 2.58 | 3.49 | 4.28
8 × 8 × ½ wall thickness | 80 | 0.77 | 1.66 | 2.44 | 3.13 | 6 double extra strong 0.864 wall thickness | 80 | 0.59 | 1.46 | 2.23 | 2.92
| 100 | 0.92 | 1.91 | 2.75 | 3.49 |  | 100 | 0.73 | 1.71 | 2.54 | 3.29
| 110 | 1 | 2.02 | 2.89 | 3.66 |  | 110 | 0.8 | 1.82 | 2.69 | 3.47
| 120 | 1.07 | 2.14 | 3.03 | 3.82 |  | 120 | 0.86 | 1.93 | 2.83 | 3.63
8 × 8 × ⅜ wall thickness | 80 | 0.91 | 1.84 | 2.63 | 3.33 | 6 extra strong 0.432 wall thickness | 80 | 0.94 | 1.9 | 2.7 | 3.42
| 100 | 1.07 | 2.08 | 2.92 | 3.67 |  | 100 | 1.1 | 2.13 | 2.98 | 3.74
| 110 | 1.14 | 2.19 | 3.06 | 3.83 |  | 110 | 1.17 | 2.23 | 3.11 | 3.89
| 120 | 1.21 | 2.29 | 3.19 | 3.98 |  | 120 | 1.24 | 2.34 | 3.24 | 4.04
8 × 8 × ¼ wall thickness | 80 | 1.1 | 2.06 | 2.86 | 3.57 | 6 standard 0.280 wall thickness | 80 | 1.14 | 2.12 | 2.93 | 3.64
| 100 | 1.25 | 2.28 | 3.13 | 3.87 |  | 100 | 1.29 | 2.33 | 3.19 | 3.94
| 110 | 1.32 | 2.38 | 3.25 | 4.02 |  | 110 | 1.36 | 2.43 | 3.31 | 4.08
| 120 | 1.39 | 2.48 | 3.38 | 4.17 |  | 120 | 1.42 | 2.53 | 3.43 | 4.22
For SI: 1 inch = 25.4 mm, 1 pound per cubic feet = 16.02 kg/m³.
Note: Tabulated values assume 1-inch air gap between masonry and steel section.

## 722.5.1(6)
TABLE 722.5.1(6)
FIRE RESISTANCE OF CLAY MASONRY PROTECTED STEEL COLUMNS
COLUMN SIZE | CLAY MASONRY DENSITY, POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CLAY MASONRY PROTECTION ASSEMBLY Tₒ (inches) |  |  |  | COLUMN SIZE | CLAY MASONRY DENSITY, POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CLAY MASONRY PROTECTION ASSEMBLY Tₒ (inches)
|  | 1 hour | 2 hours | 3 hours | 4 hours |  |  | 1 hour | 2 hours | 3 hours | 4 hours
W14 × 82 | 120 | 1.23 | 2.42 | 3.41 | 4.29 | W10 × 68 | 120 | 1.27 | 2.46 | 3.26 | 4.35
| 130 | 1.4 | 2.7 | 3.78 | 4.74 |  | 130 | 1.44 | 2.75 | 3.83 | 4.8
W14 × 68 | 120 | 1.34 | 2.54 | 3.54 | 4.43 | W10 × 54 | 120 | 1.4 | 2.61 | 3.62 | 4.51
| 130 | 1.51 | 2.82 | 3.91 | 4.87 |  | 130 | 1.58 | 2.89 | 3.98 | 4.95
W14 × 53 | 120 | 1.43 | 2.65 | 3.65 | 4.54 | W10 × 45 | 120 | 1.44 | 2.66 | 3.67 | 4.57
| 130 | 1.61 | 2.93 | 4.02 | 4.98 |  | 130 | 1.62 | 2.95 | 4.04 | 5.01
W14 × 43 | 120 | 1.54 | 2.76 | 3.77 | 4.66 | W10 × 33 | 120 | 1.59 | 2.82 | 3.84 | 4.73
| 130 | 1.72 | 3.04 | 4.13 | 5.09 |  | 130 | 1.77 | 3.1 | 4.2 | 5.13
W12 × 72 | 120 | 1.32 | 2.52 | 3.51 | 4.4 | W8 × 40 | 120 | 1.47 | 2.7 | 3.71 | 4.61
| 130 | 1.5 | 2.8 | 3.88 | 4.84 |  | 130 | 1.65 | 2.98 | 4.08 | 5.04
W12 × 58 | 120 | 1.4 | 2.61 | 3.61 | 4.5 | W8 × 31 | 120 | 1.59 | 2.82 | 3.84 | 4.73
| 130 | 1.57 | 2.89 | 3.98 | 4.94 |  | 130 | 1.77 | 3.1 | 4.2 | 5.17
W12 × 50 | 120 | 1.43 | 2.65 | 3.66 | 4.55 | W8 × 24 | 120 | 1.66 | 2.9 | 3.92 | 4.82
| 130 | 1.61 | 2.93 | 4.02 | 4.99 |  | 130 | 1.84 | 3.18 | 4.28 | 5.25
W12 × 40 | 120 | 1.54 | 2.77 | 3.78 | 4.67 | W8 × 18 | 120 | 1.75 | 3 | 4.01 | 4.91
| 130 | 1.72 | 3.05 | 4.14 | 5.1 |  | 130 | 1.93 | 3.27 | 4.37 | 5.34
STEEL TUBING | [5 empty] | STEEL PIPE
NOMINAL TUBE SIZE (inches) | CLAY MASONRY DENSITY, POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CLAY MASONRY PROTECTION ASSEMBLY Tₒ (inches) |  |  |  | NOMINAL PIPE SIZE (inches) | CLAY MASONRY DENSITY, POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CLAY MASONRY PROTECTION ASSEMBLY Tₒ (inches)
|  | 1 hour | 2 hours | 3 hours | 4 hours |  |  | 1 hour | 2 hours | 3 hours | 4 hours
4 × 4 × ½ wall thickness | 120 | 1.44 | 2.72 | 3.76 | 4.68 | 4 double extra strong 0.674 wall thickness | 120 | 1.26 | 2.55 | 3.6 | 4.52
| 130 | 1.62 | 3 | 4.12 | 5.11 |  | 130 | 1.42 | 2.82 | 3.96 | 4.95
4 × 4 × ⅜ wall thickness | 120 | 1.56 | 2.84 | 3.88 | 4.78 | 4 extra strong 0.337 wall thickness | 120 | 1.6 | 2.89 | 3.92 | 4.83
| 130 | 1.74 | 3.12 | 4.23 | 5.21 |  | 130 | 1.77 | 3.16 | 4.28 | 5.25
4 × 4 × ¼ wall thickness | 120 | 1.72 | 2.99 | 4.02 | 4.92 | 4 standard 0.237 wall thickness | 120 | 1.74 | 3.02 | 4.05 | 4.95
| 130 | 1.89 | 3.26 | 4.37 | 5.34 |  | 130 | 1.92 | 3.29 | 4.4 | 5.37
6 × 6 × ½ wall thickness | 120 | 1.33 | 2.58 | 3.62 | 4.52 | 5 double extra strong 0.750 wall thickness | 120 | 1.17 | 2.44 | 3.48 | 4.4
| 130 | 1.5 | 2.86 | 3.98 | 4.96 |  | 130 | 1.33 | 2.72 | 3.84 | 4.83
6 × 6 × ⅜ wall thickness | 120 | 1.48 | 2.74 | 3.76 | 4.67 | 5 extra strong 0.375 wall thickness | 120 | 1.55 | 2.82 | 3.85 | 4.76
| 130 | 1.65 | 3.01 | 4.13 | 5.1 |  | 130 | 1.72 | 3.09 | 4.21 | 5.18
6 × 6 × ¼ wall thickness | 120 | 1.66 | 2.91 | 3.94 | 4.84 | 5 standard 0.258 wall thickness | 120 | 1.71 | 2.97 | 4 | 4.9
| 130 | 1.83 | 3.19 | 4.3 | 5.27 |  | 130 | 1.88 | 3.24 | 4.35 | 5.32
8 × 8 × ½ wall thickness | 120 | 1.27 | 2.5 | 3.52 | 4.42 | 6 double extra strong 0.864 wall thickness | 120 | 1.04 | 2.28 | 3.32 | 4.23
| 130 | 1.44 | 2.78 | 3.89 | 4.86 |  | 130 | 1.19 | 2.6 | 3.68 | 4.67
8 × 8 × ⅜ wall thickness | 120 | 1.43 | 2.67 | 3.69 | 4.59 | 6 extra strong 0.432 wall thickness | 120 | 1.45 | 2.71 | 3.75 | 4.65
| 130 | 1.6 | 2.95 | 4.05 | 5.02 |  | 130 | 1.62 | 2.99 | 4.1 | 5.08
8 × 8 × ¼ wall thickness | 120 | 1.62 | 2.87 | 3.89 | 4.78 | 6 standard 0.280 wall thickness | 120 | 1.65 | 2.91 | 3.94 | 4.84
| 130 | 1.79 | 3.14 | 4.24 | 5.21 |  | 130 | 1.82 | 3.19 | 4.3 | 5.27

## 722.5.1(7)
TABLE 722.5.1(7)
MINIMUM COVER (inch) FOR STEEL COLUMNS ENCASED IN NORMAL-WEIGHT CONCRETEᵃ FIGURE 722.5.1(6)(c)
STRUCTURAL SHAPE | FIRE-RESISTANCE RATING (hours)
| 1 | 1½ | 2 | 3 | 4
W14 × 233 |  |  |  | 1½ | 2
× 176 |  |  | 1
× 132 | 1
× 90 |  | 1½ |  | 2
× 61
× 48 |  |  |  |  | 3
× 43
W12 × 152 |  | 1 | 1 |  | 2½
× 96 |  |  |  | 2
× 65 | 1
× 50 |  | 1½ |  | 2½ | 3
× 40
W10 × 88 | 1 |  |  | 2
× 49 |  |  |  |  | 3
× 45 | 1 | 1½ |  | 2½
× 39 |  |  |  |  | 3½
× 33 |  |  | 2
W8 × 67 |  | 1 |  |  | 3
× 58 |  |  | 1½ | 2½
× 48 | 1 |  |  |  | 3½
× 31 |  | 1½
× 21 |  |  | 2 | 3
× 18 |  |  |  |  | 4
W6 × 25 |  | 1½ | 2 | 3 | 3½
× 20 | 1
× 16 |  | 2 | 2½ | 3½ | 4
× 15 | 1½
× 9

## 722.5.1(8)
TABLE 722.5.1(8)
MINIMUM COVER (inch) FOR STEEL COLUMNS ENCASED IN STRUCTURAL LIGHTWEIGHT CONCRETEᵃ FIGURE 722.5.1(6)(c)
STRUCTURAL SHAPE | FIRE-RESISTANCE RATING (HOURS)
| 1 | 1 ½ | 2 | 3 | 4
W14 × 233 |  |  |  | 1 | 1½
× 193
× 74 | 1 | 1 | 1 |  | 2
× 61 |  |  |  | 1½
× 43 |  |  |  |  | 2½
W12 × 65 | 1 | 1 | 1 | 1½ | 2
× 53 |  |  |  |  | 2½
× 40 |  |  |  | 2
W10 × 112 | 1 | 1 |  | 1½ | 2
× 88 |  |  | 1
× 60 |  |  | 1½ | 2 | 2½
× 33
W8 × 35 |  |  |  | 2 | 2½
× 28 | 1 |  | 1½
× 24 |  |  |  | 2½ | 3
× 18 |  | 1½

## 722.5.1(9)
TABLE 722.5.1(9)
MINIMUM COVER (inch) FOR STEEL COLUMNS IN NORMAL-WEIGHT PRECAST COVERSᵃ FIGURE 722.5.1(6)(a)
STRUCTURAL SHAPE | FIRE-RESISTANCE RATING (hours)
| 1 | 1½ | 2 | 3 | 4
W14 × 233 |  |  |  | 2½ | 3
× 211 |  | 1½
× 176 |  |  |  |  | 3½
× 145
× 109 | 1½ |  |  | 3
× 99 |  |  | 2 |  | 4
× 61 |  |  | 2½ | 3½
× 43 |  |  |  |  | 4½
W12 × 190 |  | 1½ | 1½ | 2½ | 3½
× 152
× 120 | 1½ |  | 2 | 3 | 4
× 96
× 87 |  |  | 2½ | 3½
× 58 |  |  |  |  | 4½
× 40
W10 × 112 |  | 1½ | 2 | 3 | 3½
× 88
× 77 | 1½ |  | 2½ | 3½ | 4
× 54
× 33 |  |  |  | 3½ | 4½
W8 × 67 |  | 1½ | 2 | 3
× 58 |  |  |  |  | 4
× 48 | 1½ |  | 2½ | 3½
× 28 |  |  |  |  | 4½
× 21 |  |  |  | 4
× 18 |  |  |  |  | 4
W6 × 25 | 1½ | 2 | 2½ | 3½ | 4½
× 20
× 16 | 2 |  | 3 | 4
× 12 |  |  |  |  | 4½
× 9 |  |  |  |  | 5

## 722.5.1(10)
TABLE 722.5.1(10)
MINIMUM COVER (inch) FOR STEEL COLUMNS IN STRUCTURAL LIGHTWEIGHT PRECAST COVERSᵃ FIGURE 722.5.1(6)(a)
STRUCTURAL SHAPE | FIRE-RESISTANCE RATING (hours)
| 1 | 1½ | 2 | 3 | 4
W14 × 233 |  |  |  | 2 | 2½
× 176
× 145 |  |  | 1½
× 132 | 1½ | 1½ |  | 2½ | 3
× 109
× 99 |  |  | 2 | 3
× 68 |  |  |  |  | 3½
× 43
W12 × 190 | 1½ | 1½ |  | 2 | 2½
× 152
× 136 |  |  | 1½ | 2½ | 3
× 106
× 96 |  |  |  | 3 | 3½
× 87
× 65 |  |  | 2 | 3 | 3½
× 40
W10 × 112 | 1½ | 1½ |  | 2 | 3
× 100 |  |  | 1½
× 88 |  |  |  | 2½ | 3
× 77
× 60 |  |  | 2 |  | 3½
× 39 |  |  |  | 3
× 33 |  | 2 |  |  | 3½
W8 × 67 |  | 1½ | 1½ | 2½ | 3
× 48 | 1½ | 1½ |  |  | 3½
× 35 |  |  | 2 | 3
× 28
× 18 |  |  | 2½ |  | 4
W6 × 25 |  |  | 2 | 3 | 3½
× 15 | 1½ | 2 | 2½ | 3 | 4
× 9 |  |  |  | 3½ | 4

## 722.6.2(1)
TABLE 722.6.2(1)
TIME ASSIGNED TO WALLBOARD MEMBRANES*,b,c,d
DESCRIPTION OF FINISH | TIME* (minutes)
3/8-inch wood structural panel bonded with exterior glue | 5
15/32-inch wood structural panel bonded with exterior glue | 10
19/32-inch wood structural panel bonded with exterior glue | 15
3/8-inch gypsum wallboard | 10
1/2-inch gypsum wallboard | 15
5/8-inch gypsum wallboard | 30
1/2-inch Type X gypsum wallboard | 25
5/8-inch Type X gypsum wallboard | 40
Double 3/8-inch gypsum wallboard | 25
1/2- + 3/8-inch gypsum wallboard | 35
Double 1/2-inch gypsum wallboard | 40

## 722.6.2(2)
TABLE 722.6.2(2)
TIME ASSIGNED FOR CONTRIBUTION OF WOOD FRAMEa, b, c
DESCRIPTION | TIME ASSIGNED TO FRAME (minutes)
Wood studs 16 inches o.c. | 20
Wood floor and roof joists 16 inches o.c. | 10
Wood floor and roof joists 16 inches o.c. | 10

## 722.6.2(3)
TABLE 722.6.2(3)
MEMBRANEᵃ ON EXTERIOR FACE OF WOOD STUD WALLS
SHEATHING | PAPER | EXTERIOR FINISH
5/8-inch T & G lumber 5/16-inch exterior glue plywood 1/2-inch gypsum wallboard 5/8-inch gypsum wallboard 1/2-inch fiberboard | Sheathing paper | Lumber siding Wood shingles and shakes 1/4-inch fiber-cement lap, panel or shingle siding 1/4-inch wood structural panels—exterior type 1/4-inch hardboard Metal siding Stucco on metal lath Masonry veneer
None | — | 3/8-inch exterior-grade wood structural panels

## 722.6.2(4)
TABLE 722.6.2(4)
FLOORING OR ROOFING OVER WOOD FRAMINGᵃ
ASSEMBLY | STRUCTURAL MEMBERS | SUBFLOOR OR ROOF DECK | FINISHED FLOORING OR ROOFING
Floor | Wood | 15/32-inch wood structural panels or 11/16 inch T & G softwood | Hardwood or softwood flooring on building paper resilient flooring, parquet floor felted-synthetic fiber floor coverings, carpeting, or ceramic tile on 1/4-inch-thick fiber-cement underlayment or 3/8-inch-thick panel-type underlay Ceramic tile on 1 1/4-inch mortar bed
Roof | Wood | 15/32-inch wood structural panels or 11/16 inch T & G softwood | Finished roofing material with or without insulation

## 722.6.2(5)
TABLE 722.6.2(5)
TIME ASSIGNED FOR ADDITIONAL PROTECTION
DESCRIPTION OF ADDITIONAL PROTECTION | FIRE RESISTANCE (minutes)
Add to the fire-resistance rating of wood stud walls if the spaces between the studs are completely filled with glass fiber mineral wool batts weighing not less than 2 pounds per cubic foot (0.6 pound per square foot of wall surface) or rockwool or slag material wool batts weighing not less than 3.3 pounds per cubic foot (1 pound per square foot of wall surface), or cellulose insulation having a nominal density not less than 2.6 pounds per cubic foot. | 15

## 803.11
TABLE 803.11
INTERIOR WALL AND CEILING FINISH REQUIREMENTS BY OCCUPANCYᵃ
GROUP | SPRINKLEREDᶡ |  |  | NONSPRINKLERED
| Interior exit stairways, interior exit ramps and exit passagewaysᵃʷ ᵇ | Corridors and enclosure for exit access stairways and exit access ramps | Rooms and enclosed spacesᶜ | Interior exit stairways, interior exit ramps and exit passagewaysᵃʷ ᵇ | Corridors and enclosure for exit access stairways and exit access ramps | Rooms and enclosed spacesᶜ
A-1 & A-2 | B | B | C | A | Aᵈ | Bᵉ
A-3ᶠ, A-4, A-5 | B | B | C | A | Aᵈ | C
B, E, M, R-1 | B | B | B | A | A | B
F | B | C | C | A | B | B
H | B | B | Cᵍ | A | A | B
I-1 | B | C | C | A | B | B
I-2 | B | B | Bʰʷ ⁱ | A | A | B
I-3 | A | Aʲ | C | A | A | B
I-4 | B | B | Bʰʷ ⁱ | A | A | B
INTERIOR FINISHES
R-2 | B | B | C | A | A | C
R-3 | C | C | C | C | C | C
S | B | C | C | A | B | C
U | No restrictions |  |  | No restrictions

## 903.2.5.2
TABLE 903.2.5.2
GROUP H-5 SPRINKLER DESIGN CRITERIA
LOCATION | OCCUPANCY HAZARD CLASSIFICATION
Fabrication areas | Ordinary Hazard Group 2
Service corridors | Ordinary Hazard Group 2
Storage rooms without dispensing | Ordinary Hazard Group 2
Storage rooms with dispensing | Extra Hazard Group 2
Corridors | Ordinary Hazard Group 2

## 903.2.11.10
‡‡‡ TABLE 903.2.11.10
ADDITIONAL REQUIRED SUPPRESSION SYSTEMS
OCCUPANCY GROUP, SPECIFIED USE, MATERIALS OR EQUIPMENT (in alphabetical order) | CODE SECTION
Aerosol warehouses | FC 2804.4.1
Aircraft hangers | BC 412.4.6, BC 412.4.6.1, BC 412.6.5
Airport traffic control towers | BC 412.3.6
Atriums | BC 404.3
Automated storage; buildings with | FC 3209.2
Children’s play structures | BC 424.3
Chutes; refuse and laundry | BC 713.13
Chute vestibules | BC Appendix Q 22.15.2.2.1
Cold storage buildings: ice plants, food plants and food processing rooms with foam insulation up to 10 inches in thickness | BC 2603.3
Combustible fibers; storage at waterfront structures | FC 3706.6
Combustible fibers, loose; storage of more than 1,000 sq ft of | FC 3704.5
Commercial cooking systems | BC 904.12 FC 904.11
Commercial cooking systems with solid fuel storage | FC 609.5
Commercial cooking system with Type I hood | BC 904.2.1 MC 509.1
Covered mall and open mall buildings | BC 402.5
Dead-end public streets; buildings on | FC 503.3.1
Dip tank rooms | FC 2405.1
Dip tanks | FC 2405.3.4.1
Dry cleaning machines | FC 1208.3
Dry cleaning plants | FC 1208.2
Drying rooms | BC 417.4
Elevator lobbies | BC 3006.1.1
Exhausted enclosures | FC 5003.8.5
Extra-high-rack combustible storage; buildings with | FC 3208.5.1
Flammable and combustible liquid in Group H-2 or H-3 areas | FC 5705.3.7.3
Flammable and combustible liquid storage rooms | FC 5704.5.7.5.1
Flammable and combustible liquid storage warehouses | FC 3404.3.8.4
Flammable finishes | BC 416.5
Fuel-oil tanks and fuel-oil burning equipment; rooms containing | MC 1305.13.3
Furnaces: Class A and B | FC 3006.1
Furnaces: Class C and D | FC 3006.2
Gas rooms | FC 5003.8.4
Glazing in smoke partition | BC 710.2
Group H-2 | BC 415.9.1.3
Group H-5, including but not limited to: workstations, gas cabinet, exhausted enclosures, pass-throughs in exit access corridors and exhaust ducts | BC 415.11
Group I-2 | BC 407.6
Hardening and tempering tanks | FC 2405.4.4
Hazardous exhaust system ducts | MC 510.8
Hazardous materials; indoor handling or use of | FC 5005.1.8
Hazardous materials; indoor storage of | FC 5004.5
Hazardous Production Material (“HPM”) corridors | FC 2703.10.3
Hazardous Production Material (“HPM”) exhaust ducts | FC 2703.10.4
Hazardous Production Material (“HPM”) facilities | FC 2703.10
Hazardous Production Material (“HPM”) gas cabinets | FC 2703.10.2
Hazardous Production Material (“HPM”) work station exhaust | FC 2703.10.1.1
High Pressure Gas Installations; buildings with | FGC G.2.3
Highly toxic and toxic compressed gases; exhausted enclosures for | FC 6004.1.3
Highly toxic and toxic compressed gases; gas cabinets containing | FC 6004.1.2
Highly toxic and toxic compressed gases; gas rooms utilizing | FC 6004.2.2.6
Highly toxic and toxic compressed gases; outdoor storage of | FC 6004.3.3
High-rise buildings | BC 403.3
Incidental uses | BC 509.4.2
Equipment platforms | BC 505.3.2
Kiosks in covered mall buildings | BC 402.6.2
Kiosks, displays, booths, or concession stands; covered | FC 314.5.1
Laboratory units; non-production | BC 427.6.1
Liquefied petroleum gas (“LPG”) within buildings accessible to the public; storage of | FC 6109.9
Liquids, Class II and III, below grade storage of | FC 5704.3.5.1
Liquids, Class II and III, below grade storage of, accessory to retail | BC 414.2.5.1
Medical gas; storage of | FC 5306.2.1
Organic coatings; manufacturing of | BC 418.1
Oxidizer, solid and liquid; storage areas | FC 6304.1.4
Plastic light diffusing system | BC 2606.7.4
Pyroxylin plastic; areas with | FC 6504.1.1
Pyroxylin plastic; storage and manufacturing | FC 6504.2
Pyroxylin plastic; storage vaults | FC 6504.1.3
Rack storage | FC 3208.3
Radioactive materials and radiation-producing equipment; uses and occupancies involving | BC 428.3.4
Resin application areas | FC 2409.2.1
Silane gas; exhausted enclosures or gas cabinets for | FC 6404
Small arms ammunition and primers, black powder or smokeless propellant; storage of | FC 5606.7
Solid-piled and shelf storage | FC 3207.2
Smoke-protected assembly seating | BC 1029.6.2.3
Special amusement buildings | BC 411.4
Spray booths and rooms | FC 2404.3.3
Spray booths involving the use of organic peroxide coatings | FC 2408.2.2
Spray finishing in Group A, E, I or R | FC 2404.1
Stages | BC 410.7
Sterilization systems; rooms with | FC 5806.3.2
Storage | FC Table 3206.2 FC 3206.4
Substandard width public streets; buildings on | FC 503.8.2
Textile ceiling finish | BC 803
Textile wall coverings | BC 803
Underground buildings and spaces | BC 405.3
Unlimited area buildings | BC 507

## 907.5.2.3.2
TABLE 907.5.2.3.2
VISIBLE ALARMS
NUMBER OF UNITS | UNITS WITH VISIBLE ALARMS
6 to 25 | 2
26 to 50 | 4
51 to 75 | 7
76 to 100 | 9
101 to 150 | 12
151 to 200 | 14
201 to 300 | 17
301 to 400 | 20
401 to 500 | 22
501 to 1,000 | 5% of total
1,001 and over | 50 plus 3 for each 100 over 1,000

## 1004.1.3
TABLE 1004.1.3
MAXIMUM FLOOR AREA ALLOWANCES PER OCCUPANT
FUNCTION OF SPACE | OCCUPANT LOAD FACTORᵃ
Accessory storage areas, mechanical equipment room | 300 gross
Agricultural building | 300 gross
Aircraft hangars | 500 gross
Assembly Gaming floors (keno, slots, etc.) Exhibit gallery and museum | 11 gross 30 net
Assembly with fixed seats | See Section 1004.3
Assembly without fixed seats Concentrated (chairs only—not fixed) Dance floor Dance floor (ballroom) Standing space Unconcentrated (tables and chairs) | 7 net 5 net 10 net 5 net 15 net
Bowling centers, allow 5 persons for each lane including 15 feet of runway, and for additional areas | 7 net
Business areas, including accessory areas on terraces and rooftops | 100 grossᵇʷ ᵈ
Courtrooms – other than fixed seating areas | 40 net
Day Care: Age under 6 months Age 6 months – 2 years Age 2 years – 6 years Age above 6 years | 50 net 40 net 30 net 50 net
Dormitories | 50 gross
Educational Classroom area Shops and other vocational room areas Kindergarten, and pre-kindergarten | 20 net 50 net 30 net
Exercise rooms | 50 gross
Gymnasiums | 15 net
Group H-5 Fabrication and manufacturing areas | 200 gross
Industrial areas | 100 gross
Institutional areas Inpatient treatment areas Outpatient areas Sleeping areas | 240 gross 100 gross 120 gross
Kitchens, commercial | 200 gross
Library Reading rooms Stack area | 50 net 100 gross
Locker rooms | 50 gross
Mall buildings - covered and open | See Section 402.8.2
Mercantile Areas on other floors Basement and grade floor areas Storage, stock, shipping areas | 60 gross 30 gross 300 gross
Parking garages | 200 gross
Passenger terminal Baggage claim Baggage handling Concourse Passenger terminal or platform Waiting area (Standing) Waiting areas (Seated) | 20 gross 300 gross 100 gross 1.5 X C* 15 gross 5 net
Residential Within dwelling units Rooftop and terrace accessory to Groups R-2 and R-3 Indoor residential amenity spaces accessory to Group R-2 (concentrated)ᵉ Indoor residential amenity spaces accessory to Group R-2 (unconcentrated)ᵉ | 200 gross 200 grossᵇʷ ᶜʷ ᵈ 15 net 50 net
Skating rinks, swimming pools Rink and pool Decks | 50 gross 15 gross
Stages and platforms | 15 net for performing area and 50 net remaining area
Warehouses | 500 gross

## 1006.2.1
TABLE 1006.2.1
SPACES WITH ONE EXIT OR EXIT ACCESS DOORWAY
OCCUPANCY | MAXIMUM OCCUPANT LOAD OF SPACE | MAXIMUM COMMON PATH OF EGRESS TRAVEL DISTANCE (feet)
|  | Without Sprinkler System (feet) |  | With Sprinkler System (feet)
Occupant Load
|  | OL ≤ 30 | OL > 30
Aᶜ, Eᶠ, M | 74 | 76 | 75 | 75ᵃ
B | 74 | 100 | 75 | 100ᵃ
F | 49 | 75 | 75 | 100ᵃ
H-1, H-2, H-3 | 3 | NP | NP | 25ᵇ
H-4ᵇ, H-5ᵇ, I-1, I-3, I-4 | 10 | NP | NP | 75ᵃ
I-2ᵈ | See Section 407 | NP | NP | 75ᵃ
R-1 | 20 | NP | NP | 75ᵃ
R-2 | 20ᵍ | NP | NP | 125ᵃ
S | 29 | 100 | 75ᶜ | 100ᵃ
U | 74 | 100 | 75 | 75ᵃ

## 1006.3.1
TABLE 1006.3.1
MINIMUM NUMBER OF EXITS OR ACCESS TO EXITS PER STORY
OCCUPANT LOAD (persons per story) | MINIMUM NUMBER OF EXITS (per story)
1–500 | 2
501–1,000 | 3
More than 1,000 | 4

## 1006.3.2
TABLE 1006.3.2
STORIES WITH ONE EXIT OR ACCESS TO ONE EXIT
STORY | OCCUPANCY | MAXIMUM OCCUPANT LOAD PER FLOOR | MAXIMUM TRAVEL DISTANCE (feet)
First story above grade plane or cellarᶠ | A, Bᵇ, Eᶜ, Fᵇ, M, U, Sᵇ | 49 | 75
| H-2, H-3 | 3 | 25
| H-4, H-5, I, Rᵉ | 10 | 75
| Sᵃ | 29 | 100
Second story above grade plane | B, F, M, Sᵃ | 29 | 75
| R-2ᵈʷ ᵉ | NA | 50
Third story above grade plane | R-2ᵈʷ ᵉ | NA | 50

## 1010.1.4.1(1)
‡‡‡ TABLE 1010.1.4.1(1)
MAXIMUM DOOR SPEED MANUAL REVOLVING DOORS
REVOLVING DOOR MAXIMUM NOMINAL DIAMETER (FT-IN) | MAXIMUM ALLOWABLE REVOLVING DOOR SPEED (RPM)
2000-06-01 | 12
2000-07-01 | 11
2000-08-01 | 10
2000-09-01 | 9
2000-10-01 | 8

## 1010.1.4.1(2)
TABLE 1010.1.4.1(2)
MAXIMUM DOOR SPEED AUTOMATIC OR POWER-OPERATED REVOLVING DOORS
REVOLVING DOOR MAXIMUM NOMINAL DIAMETER (FT-IN) | MAXIMUM ALLOWABLE REVOLVING DOOR SPEED (RPM)
2000-08-01 | 7.2
2000-09-01 | 6.4
2000-10-01 | 5.7
2000-11-01 | 5.2
2000-12-01 | 4.8
2026-12-06 | 4.6
14-0 | 4.1
16-0 | 3.6
17-0 | 3.4
18-0 | 3.2
20-0 | 2.9
24-0 | 2.4

## 1017.2
TABLE 1017.2
EXIT ACCESS TRAVEL DISTANCEᵃ
OCCUPANCY | WITHOUT SPRINKLER SYSTEM (feet) | WITH SPRINKLER SYSTEM (feet)
A | See Section 1029.7
E, F-1, M, R, S-1 | 150 | 200ᵇ
B | 200 | 300ᶜ
F-2, S-2, U | 200 | 250ᶜ
H-1 | Not Permitted | 75ᵈ
H-2 | Not Permitted | 100ᵈ
H-3 | Not Permitted | 150ᵈ
H-4 | Not Permitted | 175ᵈ
H-5 | Not Permitted | 200ᵉ
I-1, I-2, I-3, I-4 | Not Permitted | 200c

## 1020.1.1
TABLE 1020.1.1
INTERIOR CORRIDOR FIRE-RESISTANCE RATING
OCCUPANCY | OCCUPANT LOAD SERVED BY INTERIOR CORRIDOR | REQUIRED FIRE-RESISTANCE RATING (hours)
|  | Without sprinkler system | With sprinkler systemᶜ
H-1, H-2, H-3 | All | Not Permitted | 1
H-4, H-5 | Greater than 30 | Not Permitted | 1
A, B, E, F, M, S, U | Greater than 30 | 1 | 0
R | Greater than 10 | 1ᵈ | 0
I-2ᵃ, I-4 | All | Not Permitted | 0
I-1, I-3 | All | Not Permitted | 1ᵇ

## 1020.1.2
TABLE 1020.1.2
PUBLIC CORRIDOR FIRE-RESISTANCE RATING
OCCUPANCY | REQUIRED FIRE-RESISTANCE RATING (hours)
H-1. H-2. H-3 | 2
H-4, H-5 | 1
A, E, F, M, S, U | 1
B | 1ᵃ
R (Noncombustible) | 1ᶜ
R (Combustible) | 2ᵇ
I-1, I-2, I-3, I-4 | 1

## 1020.2
TABLE 1020.2
MINIMUM CORRIDOR WIDTH
OCCUPANCY | MINIMUM WIDTH (inches)
Any facilities not listed below | 44
Access to and utilization of mechanical, plumbing or electrical systems or equipment | 24
With an occupant load of 50 or less, except as otherwise required by Chapter 11 | 36
Within a dwelling unit, in Occupancy Groups I-1 and R-1, except as otherwise required by Section 1107 | 36
Within a dwelling unit, in Occupancy Groups R-2 and R-3, except as otherwise required by Section 1107 | 30
In Group E serving classrooms | 66
In corridors and areas serving stretcher traffic in occupancies where patients receive outpatient medical care that causes the patients to be incapable of self-preservation | 72
Group I-2 in areas where required for bed movement | 96

## 1029.6.2
TABLE 1029.6.2
CAPACITY FOR AISLES FOR SMOKE-PROTECTED ASSEMBLY
TOTAL NUMBER OF SEATS IN THE SMOKE- PROTECTED ASSEMBLY SEATING | INCHES OF CLEAR WIDTH PER SEAT SERVED
| Stepped aisles with handrails within 30 inches | Stepped aisles without handrails within 30 inches | Level aisles or ramped aisles not steeper than 1 in 10 in slope | Ramped aisles-steeper than 1 in 10 in slope
Equal to or less than 5,000 | 0.2 | 0.25 | 0.15 | 0.165
10000 | 0.13 | 0.163 | 0.1 | 0.11
15000 | 0.096 | 0.12 | 0.07 | 0.077
20000 | 0.076 | 0.095 | 0.056 | 0.062
Equal to or greater than 25,000 | 0.06 | 0.075 | 0.044 | 0.048

## 1029.7
TABLE 1029.7
TRAVEL DISTANCE
OCCUPANCY | NON-SPRINKLERED |  | SPRINKLERED
| PRIMARY | SECONDARY | PRIMARY | SECONDARY
A-1, A-2, A-3, A-4 | 100 | 150 | 150 | 250
A-5 | 200 | 300 | 200 | 300

## 1029.12.2.1
TABLE 1029.12.2.1
SMOKE-PROTECTED ASSEMBLY AISLE ACCESSWAYS
TOTAL NUMBER OF SEATS IN THE SMOKE-PROTECTED ASSEMBLY SEATING | MAXIMUM NUMBER OF SEATS PER ROW PERMITTED TO HAVE A MINIMUM 12-INCH CLEAR WIDTH AISLE ACCESSWAY
Aisle or doorway at both ends of row
| Seats with backrests | Seats without backrests
Less than 4,000 | 14 | 21
4000 | 15 | 22
7000 | 16 | 23
10000 | 17 | 24
13000 | 18 | 25
16000 | 19 | 26
19000 | 20 | 27
22,000 and greater | 21 | 28

## 1105.1.8
TABLE 1105.1.8
PUBLIC ENTRANCE WITH POWER-OPERATED DOORS
OCCUPANCY | OCCUPANT LOAD ≥
A-1, A-2, A-3, A-4, B, R-1 | 200
E, M | 300

## 1106.7.3
‡‡‡ TABLE 1106.7.3
VALET AND ATTENDED ACCESSIBLE PARKING SPACES
TOTAL PARKING SPACES PROVIDED IN PARKING FACILITIES | REQUIRED MINIMUM NUMBER OF ACCESSIBLE SPACES
1 to 25 | 1
26 to 50 | 2
51 to 75 | 3
76 to 100 | 4
101 to 150 | 5
151 to 200 | 6
201 to 300 | 7
301 to 400 | 8
401 to 500 | 9
501 to 1,000 | 2% of total
1,001 and over | 20, plus one for each 100, or fraction thereof, over 1,000

## 1107.6.1.1
TABLE 1107.6.1.1
ACCESSIBLE DWELLING UNITS AND SLEEPING UNITS
TOTAL NUMBER OF UNITS PROVIDED | MINIMUM REQUIRED NUMBER OF ACCESSIBLE UNITS WITHOUT ROLL-IN SHOWERS | MINIMUM REQUIRED NUMBER OF ACCESSIBLE UNITS WITH ROLL-IN SHOWERS | TOTAL NUMBER OF REQUIRED ACCESSIBLE UNITS
1 to 25 | 1 | 0 | 1
26 to 50 | 2 | 0 | 2
51 to 75 | 3 | 1 | 4
76 to 100 | 4 | 1 | 5
101 to 150 | 5 | 2 | 7
151 to 200 | 6 | 2 | 8
201 to 300 | 7 | 3 | 10
301 to 400 | 8 | 4 | 12
401 to 500 | 9 | 4 | 13
501 to 1,000 | 2% of total | 1% of total | 3% of total
Over 1,000 | 20, plus 1 for each 100, or fraction thereof, over 1,000 | 10 plus 1 for each 100, or fraction thereof, over 1,000 | 30 plus 2 for each 100, or fraction thereof, over 1,000

## 1108.2.2.1
TABLE 1108.2.2.1
ACCESSIBLE WHEELCHAIR SPACES
CAPACITY OF SEATING IN ASSEMBLY AREAS | MINIMUM REQUIRED NUMBER OF WHEELCHAIR SPACES
4 to 25 | 1
26 to 50 | 2
51 to 100 | 4
101 to 300 | 5
301 to 500 | 6
501 to 5,000 | 6, plus 1 for each 150, or fraction thereof, between 501 through 5,000
5,001 and over | 36 plus 1 for each 200, or fraction thereof, over 5,000

## 1108.2.7.1
TABLE 1108.2.7.1
RECEIVERS FOR ASSISTIVE LISTENING SYSTEMS
CAPACITY OF SEATING IN ASSEMBLY AREAS | MINIMUM REQUIRED NUMBER OF RECEIVERS | MINIMUM NUMBER OF RECEIVERS TO BE HEARING-AID COMPATIBLE
50 or less | 2 | 2
51 to 200 | 2, plus 1 per 25 seats over 50 seats* | 2
201 to 500 | 2, plus 1 per 25 seats over 50 seats.* | 1 per 4 receivers*
501 to 1,000 | 20, plus 1 per 33 seats over 500 seats* | 1 per 4 receivers*
1,001 to 2,000 | 35, plus 1 per 50 seats over 1,000 seats* | 1 per 4 receivers*
Over 2,000 | 55, plus 1 per 100 seats over 2,000 seats* | 1 per 4 receivers*

## 1108.3
TABLE 1108.3
ACCESSIBLE SELF-SERVICE STORAGE FACILITIES
TOTAL SPACES IN FACILITY | MINIMUM NUMBER OF REQUIRED ACCESSIBLE SPACES
1 to 200 | 5%, but not less than 1
Over 200 | 10, plus 2% of total number of units over 200

## 1109.12.2
TABLE 1109.12.2
ACCESSIBLE CHECK-OUT AISLES
TOTAL CHECK-OUT AISLES OF EACH FUNCTION | MINIMUM NUMBER OF ACCESSIBLE CHECK-OUT AISLES OF EACH FUNCTION
1 to 4 | 1
5 to 8 | 2
9 to 15 | 3
Over 15 | 3, plus 20% of additional aisles

## 1110.4.9.1
TABLE 1110.4.9.1
BOAT SLIPS
TOTAL NUMBER OF BOAT SLIPS PROVIDED | MINIMUM NUMBER OF REQUIRED ACCESSIBLE BOAT SLIPS
1 to 25 | 1
26 to 50 | 2
51 to 100 | 3
101 to 150 | 4
151 to 300 | 5
301 to 400 | 6
401 to 500 | 7
501 to 600 | 8
601 to 700 | 9
701 to 800 | 10
801 to 900 | 11
901 to 1000 | 12
1001 and over | 12, plus 1 for every 100, or fraction thereof, over 1,000

## 1203.3
TABLE 1203.3
INSULATION FOR CONDENSATION CONTROL
CLIMATE ZONE | MINIMUM R-VALUE OF AIR-IMPERMEABLE INSULATIONᵃ
2B and 3B tile roof only | 0 (none required)
1, 2A, 2B, 3A, 3B, 3C | R-5
4C | R-10
4A, 4B | R-15
5 | R-20
6 | R-25
7 | R-30
8 | R-35

## 1204.1
TABLE 1204.1
MINIMUM SPACE TEMPERATURE REQUIREMENTSᵃ
ROOMS OR SPACES | MINIMUM TEMPERATURE (°F)
Habitable rooms in all buildings | 68
Building equipment and machinery rooms | 50
Patients’ rooms, bathrooms and toilet rooms, stairs and corridors in hospitals and nursing homes | As per the New York State Health Code
Bathrooms and toilet rooms except patients’ bathrooms and toilet rooms in hospitals and nursing homes | 68
Offices, waiting rooms, art galleries, museums, libraries, meeting rooms, houses of worship, classrooms, auditoriums, lecture halls, nightclubs, restaurants, theatres, locker rooms, dressing rooms, and spaces where persons are engaged in sedentary activities | 68
Laboratories, light machine work, product inspections, loft buildings, shops, stores, display rooms, show rooms, sales rooms, and spaces where persons are engaged in moderate physical activities | 65
Gymnasia, dance halls, skating rinks, bowling alleys, heavy assembly workrooms or shops, and spaces where persons are engaged in vigorous physical activities | 60
Automotive repair shops | 50
Storage areas, garages, space where work or process requires a low temperature | None
Hospital operating rooms, and recovery, labor, delivery, and nursery rooms | As per the New York State Health Code
Swimming pools, bath houses, and shower rooms | 75

## 1207.2.1
TABLE 1207.2.1
MAXIMUM SOUND PRESSURE LEVELS FOR MACHINE ROOMS ADJACENT TO DWELLING UNITS, MEASURED IN THE DWELLING UNIT
OCTAVE BANDS, HZ MID-FREQUENCY | MAXIMUM SOUND PRESSURE LEVEL dbᵃ
db re 0.0002 microbars
63 | 61
125 | 53
250 | 46
500 | 40
1000 | 36
2000 | 34
4000 | 33
8000 | 32

## Center Frequency
Center frequency of one-third octave band: | 40/125 | 160/250 | 215/500 | 630/1,000 | 1,000/10,000
Increase in sound pressure level (db): | 6 | 4 | 3 | 2 | 1½

## 1405.2
TABLE 1405.2
MINIMUM THICKNESS OF WEATHER COVERINGS
COVERING TYPE | MINIMUM THICKNESS (inches)
Adhered masonry veneer* | 0.25
Aluminum siding | 0.019
Anchored masonry veneer | 2.625
Asbestos-cement boards | 0.125
Asbestos shingles | 0.156
Cold-rolled copperᵈ | 0.0216 nominal
Copper shinglesᵈ | 0.0162 nominal
Exterior plywood (with sheathing) | 0.313
Exterior plywood (without sheathing) | See Section 2304.6
Fiber cement lap siding | 0.25ᶜ
Fiber cement panel siding | 0.25ᶜ
Fiberboard siding | 0.5
Glass-fiber reinforced concrete panels | 0.375
Hardboard sidingᶜ | 0.25
High-yield copperᵈ | 0.0162 nominal
Lead-coated copperᵈ | 0.0216 nominal
Lead-coated high-yield copper | 0.0162 nominal
Marble slabs | 1
Particleboard (with sheathing) | See Section 2304.6
Particleboard (without sheathing) | See Section 2304.6
Porcelain tile | 0.25
Steel (approved corrosion resistant) | 0.0149
Stone (cast artificial, anchored) | 1.5
Stone (natural) | 2
Structural glass | 0.344
Stucco or exterior cement plaster Three-coat work over: Metal plaster base Unit masonry Cast-in-place or precast concrete | 0.875ᵇ 0.625ᵇ 0.625ᵇ
Two-coat work over: Unit masonry Cast-in-place or precast concrete | 0.5ᵇ 0.375ᵇ
Terra cotta (anchored) | 1
Terra cotta (adhered) | 0.25
Vinyl siding | 0.035
Wood shingles | 0.375
Wood siding (without sheathing)ᵃ | 0.5

## 1406.2.1.1.2
TABLE 1406.2.1.1.2
MINIMUM FIRE SEPARATION FOR COMBUSTIBLE EXTERIOR WALL COVERINGS
FIRE SEPARATION DISTANCE (feet) | TOLERABLE LEVEL INCIDENT RADIANT HEAT ENERGY (kW/m²) | FIRE SEPARATION DISTANCE (feet) | TOLERABLE LEVEL INCIDENT RADIANT HEAT ENERGY (kW/m²)
5 | 12.5 | 16 | 5.9
6 | 11.8 | 17 | 5.5
7 | 11 | 18 | 5.2
8 | 10.3 | 19 | 4.9
9 | 9.6 | 20 | 4.6
10 | 8.9 | 21 | 4.4
11 | 8.3 | 22 | 4.1
12 | 7.7 | 23 | 3.9
13 | 7.2 | 24 | 3.7
14 | 6.7 | 25 | 3.5
15 | 6.3

## 1504.1.1
TABLE 1504.1.1
CLASSIFICATION OF ASPHALT SHINGLES
MAXIMUM ALLOWABLE STRESS DESIGN WIND SPEED, Vasd | MAXIMUM BASIC DESIGN WIND SPEED, V, FROM TABLE 1609.3 | ASTM D 7158ᵃ CLASSIFICATION | ASTM D 3161 CLASSIFICATION
88 | 110 | D, G or H | A, D or F
94 | 117 | G or H | A, D or F
102 | 127 | G or H | F
106 | 132 | G or H | F

## 1505.1
TABLE 1505.1ᵃʷ ᵇ
MINIMUM ROOF COVERING CLASSIFICATION FOR TYPES OF CONSTRUCTION
IA | IB | IIA | IIB | IIIA | IIIB | IV | VA | VB
B | B | B | B | B | B | B | B | Cᵇ

## 1507.2.9.2
TABLE 1507.2.9.2
VALLEY LINING MATERIAL
MATERIAL | MINIMUM THICKNESS | GAGE | WEIGHT
Aluminum | 0.024 in. | — | —
Cold-rolled copper | 0.0216 in. | — | ASTM B 370, 16 oz. per square ft.
Copper | — | — | 16 oz.
Galvanized steel | 0.0179 in. | 26 (zinc-coated G90) | —
High-yield copper | 0.0162 in. | — | ASTM B 370, 12 oz. per square ft.
Lead | — | — | 2.5 pounds
Lead-coated copper | 0.0216 in. | — | ASTM B 101, 16 oz. per square ft.
Lead-coated high-yield copper | 0.0162 in. | — | ASTM B 101, 12 oz. per square ft.
Painted terne | — | — | 20 pounds
Stainless steel | — | 28 | —
Zinc alloy | 0.027 in. | — | —

## 1507.3.7
TABLE 1507.3.7
CLAY AND CONCRETE TILE ATTACHMENTᵃʷ ᵇʷ ᶜ
GENERAL — CLAY OR CONCRETE ROOF TILE
Maximum Nominal Design Wind Speed, Vasdᶠ (mph) | Mean roof height (feet) | Roof slope < 3:12 | Roof slope 3:12 and over
85 | 0–60 | One fastener per tile. Flat tile without vertical laps, two fasteners per tile.
100 | 0–40
100 | > 40–60 | The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails. The nose of all ridge, hip and rake tiles shall be set in a bead of roofer’s mastic.
110 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
120 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
130 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
All | > 60 | The fastening system shall resist the wind forces in Section 1609.5.3.
INTERLOCKING CLAY OR CONCRETE ROOF TILE WITH PROJECTING ANCHOR LUGSᵈʷ ᵉ
(Installations on spaced/solid sheathing with battens or spaced sheathing)
Maximum Nominal Design Wind Speed, Vasdᶠ (mph) | Mean roof height (feet) | Roof slope < 5:12 | Roof slope 5:12 < 12:12 | Roof slope 12:12 and over
85 | 0–60
100 | 0–40 | Fasteners are not required. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile. | One fastener per tile every other row. All perimeter tiles require one fastener. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile. | One fastener required for every tile. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile.
100 | > 40–60 | The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails. The nose of all ridge, hip and rake tiles shall be set in a bead of roofer’s mastic.
110 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
120 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
130 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
All | > 60 | The fastening system shall resist the wind forces in Section 1609.5.3.
INTERLOCKING CLAY OR CONCRETE ROOF TILE WITH PROJECTING ANCHOR LUGS
(Installations on solid sheathing without battens)
Maximum Nominal Design Wind Speed, Vasdᶠ (mph) | Mean roof height (feet) | All roof slopes
85 | 0–60 | One fastener per tile.
100 | 0–40 | One fastener per tile.
100 | > 40–60 | The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails. The nose of all ridge, hip and rake tiles shall be set in a bead of roofer’s mastic.
110 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
120 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
130 | 0–60 | The fastening system shall resist the wind forces in Section 1609.5.3.
All | > 60 | The fastening system shall resist the wind forces in Section 1609.5.3.

## 1507.4.3(1)
TABLE 1507.4.3(1)
METAL ROOF COVERINGS
ROOF COVERING TYPE | STANDARD APPLICATION RATE/THICKNESS
Aluminum | ASTM B 209, 0.024 inch minimum thickness for roll-formed panels and 0.019 inch minimum thickness for press-formed shingles.
Aluminum-zinc alloy coated steel | ASTM A 792 AZ 50
Cold-rolled copper | ASTM B 370 minimum 16 oz./sq. ft. and 12 oz./sq. ft. high yield copper for metal-sheet roof covering systems: 12 oz./sq. ft. for pre-formed metal shingle systems.
Copper | 16 oz./sq. ft. for metal-sheet roof-covering systems; 12 oz./sq. ft. for preformed metal shingle systems.
Galvanized steel | ASTM A 653 G-90 zinc-coatedᵃ
Hard lead | 2 lbs./sq. ft.
Lead-coated copper | ASTM B 101
Prepainted steel | ASTM A 755
Soft lead | 3 lbs./sq. ft.
Stainless steel | ASTM A 240, 300 Series Alloys
Steel | ASTM A 924
Terne and terne-coated stainless | Terne coating of 40 lbs. per double base box, field painted where applicable in accordance with manufacturer’s instructions.
Zinc | 0.027 inch minimum thickness; 99.995% electrolytic high grade zinc with alloy additives of copper (0.08% - 0.20%), titanium (0.07% - 0.12%) and aluminum (0.015%).

## 1507.4.3(2)
TABLE 1507.4.3(2)
MINIMUM CORROSION RESISTANCE
MATERIAL | STANDARD
55% Aluminum-zinc alloy coated steel | ASTM A 792 AZ 50
5% Aluminum alloy-coated steel | ASTM A 875 GF60
Aluminum-coated steel | ASTM A 463 T2 65
Galvanized steel | ASTM A 653 G-90
Prepainted steel | ASTM A 755a

## 1507.7.6
TABLE 1507.7.6
SLATE SHINGLE HEADLAP
SLOPE | HEADLAP (inches)
4:12 < slope < 8:12 | 4
8:12 < slope < 20:12 | 3
slope ≥ 20:12 | 2

## 1507.8
TABLE 1507.8
WOOD SHINGLE AND SHAKE INSTALLATION
ROOF ITEM | WOOD SHINGLES | WOOD SHAKES
1. Roof slope | Wood shingles shall be installed on slopes of not less than three units vertical in 12 units horizontal (3:12). | Wood shakes shall be installed on slopes of not less than four units vertical in 12 units horizontal (4:12).
2. Deck requirement
Temperate climate | Shingles shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not less than 1" × 4" nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners. | Shakes shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not less than 1" × 4" nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners. When 1" × 4" spaced sheathing is installed at 10 inches, boards must be installed between the sheathing boards.
Ice forming along the eaves causing a backup of water. | Solid sheathing required. | Solid sheathing is required.
3. Interlayment | No requirements. | Interlayment shall comply with ASTM D 226, Type 1.
4. Underlayment
Temperate climate | Underlayment shall comply with ASTM D 226, Type 1. | Underlayment shall comply with ASTM D 226, Type 1.
Ice forming along the eaves causing a backup of water. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall extend from the eave's edge to a point at least 24 inches inside the exterior wall line of the building. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall extend from the lowest eave's edge of all roof surfaces to a point at least 24 inches inside the exterior wall line of the building.
5. Application
Attachment | Fasteners for wood shingles shall be hot-dipped galvanized or Type 304 (Type 316 for coastal areas) stainless steel with a minimum penetration of 0.75 inch into the sheathing. For sheathing less than 0.5 inch thick, the fasteners shall extend through the sheathing. | Fasteners for wood shakes shall be hot-dipped galvanized or Type 304 (Type 316 for coastal areas) with a minimum penetration of 0.75 inch into the sheathing. For sheathing less than 0.5 inch thick, the fasteners shall extend through the sheathing.
No. of fasteners | Two per shingle. | Two per shake.
Exposure | Weather exposures shall not exceed those set forth in Table 1507.8.7. | Weather exposures shall not exceed those set forth in Table 1507.9.8.
Method | Shingles shall be laid with a side lap of not less than 1.5 inches between joints in courses, and no two joints in any three adjacent courses shall be in direct alignment. Spacing between shingles shall be 0.25 to 0.375 inch. | Shakes shall be laid with a side lap of not less than 1.5 inches between joints in adjacent courses. Spacing between shakes shall not be less than 0.375 inch or more than 0.625 inch for shakes and taper sawn shakes of naturally durable wood and shall be 0.25 to 0.375 inch for preservative-treated taper sawn shakes.
Flashing | In accordance with Section 1507.8.8. | In accordance with Section 1507.9.9.

## 1507.8.5
TABLE 1507.8.5
WOOD SHINGLE MATERIAL REQUIREMENTS
MATERIAL | APPLICABLE MINIMUM GRADES | GRADING RULES
Wood shingles of naturally durable wood | 1, 2 or 3 | CSSB

## 1507.8.7
TABLE 1507.8.7
WOOD SHINGLE WEATHER EXPOSURE AND ROOF SLOPE
ROOFING MATERIAL | LENGTH (inches) | GRADE | EXPOSURE (inches)
|  |  | 3:12 pitch to < 4:12 | 4:12 pitch or steeper
Shingles of naturally durable wood | 16 | No. 1 | 3.75 | 5
|  | No. 2 | 3.5 | 4
|  | No. 3 | 3 | 3.5
| 18 | No. 1 | 4.25 | 5.5
|  | No. 2 | 4 | 4.5
|  | No. 3 | 3.5 | 4
| 24 | No. 1 | 5.75 | 7.5
|  | No. 2 | 5.5 | 6.5
|  | No. 3 | 5 | 5.5

## 1507.9.6
TABLE 1507.9.6
WOOD SHAKE MATERIAL REQUIREMENTS
MATERIAL | MINIMUM GRADES | APPLICABLE GRADING RULES
Wood shakes of naturally durable wood | 1 | CSSB
Taper sawn shakes of naturally durable wood | 1 or 2 | CSSB
Preservative-treated shakes and shingles of naturally durable wood | 1 | CSSB
Fire-retardant-treated shakes and shingles of naturally durable wood | 1 | CSSB
Preservative-treated taper sawn shakes of Southern pine treated in accordance with AWPA U1 (Commodity Specification A, Use Category 3B and Section 5.6) | 1 or 2 | TFS

## 1507.9.8
TABLE 1507.9.8
WOOD SHAKE WEATHER EXPOSURE AND ROOF SLOPE
ROOFING MATERIAL | LENGTH (inches) | GRADE | EXPOSURE (inches) 4:12 PITCH OR STEEPER
Shakes of naturally durable wood | 18 | No. 1 | 7.5
| 24 | No. 1 | 10ᵃ
Preservative-treated taper sawn shakes of Southern yellow pine | 18 | No. 1 | 7.5
|  | No. 1 | 10
| 18 | No. 2 | 5.5
|  | No. 2 | 7.5
Taper sawn shakes of naturally durable wood | 18 | No. 1 | 7.5
|  | No. 1 | 10
| 18 | No. 2 | 5.5
|  | No. 2 | 7.5

## 1507.10.2
TABLE 1507.10.2
BUILT-UP ROOFING MATERIAL STANDARDS
MATERIAL STANDARD | STANDARD
Acrylic coatings used in roofing | ASTM D 6083
Aggregate surfacing | ASTM D 1863
Asphalt adhesive used in roofing | ASTM D 3747
Asphalt cements used in roofing | ASTM D 3019; D 2822; D 4586
Asphalt-coated glass fiber base sheet | ASTM D 4601
Asphalt coatings used in roofing | ASTM D 1227; D 2823; D 2824; D 4479
Asphalt glass felt | ASTM D 2178
Asphalt primer used in roofing | ASTM D 41
Asphalt-saturated and asphalt-coated organic felt base sheet | ASTM D 2626
Asphalt-saturated organic felt (perforated) | ASTM D 226
Asphalt used in roofing | ASTM D 312
Coal-tar cements used in roofing | ASTM D 4022; D 5643
Coal-tar saturated organic felt | ASTM D 227
Coal-tar pitch used in roofing | ASTM D 450; Type I or II
Coal-tar primer used in roofing, damproofing and waterproofing | ASTM D 43
Glass mat, coal tar | ASTM D 4990
Glass mat, venting type | ASTM D 4897
Mineral-surfaced inorganic cap sheet | ASTM D 3909
Thermoplastic fabrics used in roofing | ASTM D 5665, D 5726

## 1507.14.3
TABLE 1507.14.3
PROTECTIVE COATING MATERIAL STANDARDS
MATERIAL | STANDARD
Acrylic coating | ASTM D 6083
Silicone coating | ASTM D 6694
Moisture-cured polyurethane coating | ASTM D 6947

## 1508.2
TABLE 1508.2
MATERIAL STANDARDS FOR ROOF INSULATION
MATERIAL | STANDARD
Cellular glass board | ASTM C 552
Composite boards | ASTM C 1289, Type III, IV, V or VI
Expanded polystyrene | ASTM C 578
Extruded polystyrene | ASTM C 578
Fiber-reinforced gypsum board | ASTM C 1278
Glass-faced gypsum board | ASTM C 1177
Mineral fiber insulation board | ASTM C 726
Perlite board | ASTM C 728
Polyisocyanurate board | ASTM C 1289, Type I or II
Wood fiberboard | ASTM C 208

## 1604.3
‡‡‡TABLE 1604.3
DEFLECTION LIMITSa, b, c, h, i
CONSTRUCTION | L or Lr | S or Wf | D + Ld, g
Roof members:c
Supporting plaster or stucco ceiling | l/360 | l/360 | l/240
Supporting nonplaster ceiling | l/240 | l/240 | l/180
Not supporting ceiling | l/180 | l/180 | l/120
Floor members | l/360 | — | l/240
Exterior walls:
With plaster or stucco finishes | — | l/360 | —
With other brittle finishes | — | l/240 | —
With flexible finishes | — | l/120 | —
Interior partitions:b
With plaster or stucco finishes | l/360 | — | —
With other brittle finishes | l/240 | — | —
With flexible finishes | l/120 | — | —
Farm buildings | — | — | l/180
Greenhouses | — | — | l/120

## 1604.5
TABLE 1604.5
RISK CATEGORY OF BUILDINGS AND OTHER STRUCTURES
RISK CATEGORY | NATURE OF OCCUPANCY
I | Buildings and other structures that represent a low risk to human life in the event of failure, including but not limited to: 1. Agricultural facilities. 2. Certain temporary facilities. 3. Minor storage facilities.
II | Buildings and other structures except those listed in Risk Categories I, III and IV.
III | Buildings and other structures that represent a substantial hazard to human life in the event of failure, including but not limited to: 1. Buildings and other structures whose primary occupancy is Places of Assembly with an occupant load greater than 300. 2. Buildings and other structures containing a Group E occupancy with an occupant load greater than 250. 3. Buildings and other structures containing educational occupancies for students above the 12th grade with an occupant load greater than 500. 4. Group I-2 occupancies with an occupant load of 50 or more resident care recipients but not having surgery or emergency treatment facilities. 5. Group I-3 occupancies. 6. Any other occupancy with an occupant load greater than 5,000ᵃ. 7. Power-generating stations, water treatment facilities for potable water, waste water treatment facilities and other public utility facilities not included in Risk Category IV. 8. Buildings and other structures not included in Risk Category IV containing quantities of toxic or explosive materials that: Exceed maximum allowable quantities per control area as given in Table 307.1(1) or 307.1(2), or per outdoor control area in accordance with the New York City Fire Code; and Are sufficient to pose a threat to the public if released.ᵇ
IV | Buildings and other structures designed as essential facilities, including but not limited to: 1. Group I-2 occupancies having surgery or emergency treatment facilities. 2. Fire, rescue, ambulance and police stations and emergency vehicle garages. 3. Designated earthquake, hurricane or other emergency shelters. 4. Designated emergency preparedness, communications and operations centers and other facilities required for emergency response. 5. Power-generating stations and other public utility facilities required as emergency backup facilities for Risk Category IV structures. 6. Buildings and other structures containing quantities of highly toxic materials that: Exceed maximum allowable quantities per control area as given in Table 307.1(2) or per outdoor control area in accordance with the New York City Fire Code; and Are sufficient to pose a threat to the public if releasedᵇ 7. Aviation control towers, air traffic control centers and emergency aircraft hangars. 8. Buildings and other structures having critical national defense functions. 9. Water storage facilities and pump structures required to maintain water pressure for fire suppression.

## 1607.1
TABLE 1607.1
‡‡‡ MINIMUM UNIFORMLY DISTRIBUTED LIVE LOADS, Lo, AND MINIMUM CONCENTRATED LIVE LOADSg
OCCUPANCY OR USE | UNIFORM (psf) | CONCENTRATED (pounds)
1. Apartments (see residential) | — | —
2. Access floor systems Office use Computer use | 50 100 | 2,000 2,000
3. Armories and drill rooms | 150ⁿ | —
4. Assembly areas Fixed seats (fastened to floor) Follow spot, projections and control rooms Lobbies Movable seats Private assembly spaces, including conference rooms Stage floors Platforms (assembly) Other assembly spaces | 60ᵐ 50 100ᵐ 100ᵐ 50 150ᵐ 100ᵐ 100ᵐ | —
5. Balconies and Decksh | 1.5 times the live load for the occupancy served. Not required to exceed 100 psf | —
6. Catwalks | 40 | 300
7. Cornices | 60 | —
8. Corridors First floor Other floors | 100 Same as occupancy served except as indicated | —
9. Dining rooms and restaurants | 100ᵐ | —
10. Dwellings (see residential) | — | —
11. Elevator machine room and control room grating (on area of 2 inches by 2 inches) | — | 300
12. Equipment rooms, including pump rooms, generator rooms, transformer vaults, and areas for switch gear, ventilating, air conditioning, and similar electrical and mechanical equipment | 75 | —
13. Finish light floor plate construction (on area of 1 inch by 1 inch) | — | 200
14. Fire escapes (exterior) On single-family dwellings only | 100 40 | —
15. Garages (passenger vehicles only) Trucks and buses | 40ᵒ See Section 1607.7 | Note a
16. Handrails, guards and grab bars | See Section 1607.8
17. Helipads | See Section 1607.6
18. Hospitals Corridors above first floor Operating rooms, laboratories Patient rooms | 80 60 40 | 1,000 1,000 1,000
19. Hotels (see residential) | — | —
20. Libraries Corridors above first floor Reading rooms Stack rooms | 80 60 150b, n | 1,000 1,000 1,000
21. Manufacturing Heavy Light | 250n 125n | 3,000 2,000
22. Marquees, except one- and two-family dwellings | 75 | —
23. Office buildings Corridors above first floor File and computer rooms shall be designed for heavier loads based on anticipated occupancy Lobbies and first-floor corridors Offices | 80 — 100 50 | 2,000 — 2,000 2,000
24. Penal institutions Cell blocks Corridors | 40 100 | — —
25. Recreational uses: Bowling alleys, poolrooms and similar uses Dance halls and ballrooms Gymnasiums Ice skating rink Reviewing stands, grandstands and bleachers Roller skating rink Stadiums and arenas with fixed seats (fastened to floor) | 75m 100m 100m 250n 100c, m 100m 60c, m | —
26. Residential One- and two-family dwellings Uninhabitable attics without storagei Uninhabitable attics with storagei, j, k Habitable attics and sleeping areask Canopies, including marquees All other areas Hotels and multifamily dwellings Private rooms and corridors serving them Public roomsm and corridors serving them | 10 20 30 20 40 40 100 | —
27. Roofs All roof surfaces subject to maintenance workers Awnings and canopies: Fabric construction supported by a skeleton structure All other construction, except one- and two-family dwellings Ordinary flat, pitched, and curved roofs (that are not occupiable) Primary roof members exposed to a work floor Single panel point of lower chord of roof trusses or any point along primary structural members supporting roofs over manufacturing, storage warehouses, and repair garages All other primary roof members Occupiable roofs: Roof gardens Assembly areas All other similar areas | 5m 20 20 100 100m Note l | 300 2,000 300 Note l
28. Schools Classrooms Corridors above the first floor First-floor corridors | 40 80 100 | 1,000 1,000 1,000
29. Scuttles, skylight ribs and accessible ceilings | — | 200
30. Sidewalks, vehicular driveways and yards, subject to trucking | 300d, m | 8,000e or 20,000d
31. Stairs and exits One- and two-family dwellings All other | 40 100 | 300f 300f
32. Storage warehouses (shall be designed for heavier loads if required for anticipated storage) Heavy Light | 250n 125n | —
33. Stores Retail First floor Upper floors Wholesale, all floors | 100 75 125n | 1,000 1,000 1,000
34. Vehicle barriers | See Section 1607.9
35. Walkways and elevated platforms (other than exitways) | 60 | —
36. Yards and terraces, pedestrians | 100m | —

## 1607.5
TABLE 1607.5
EQUIVALENT UNIFORM PARTITION LOADS
PARTITION WEIGHT (plf) | EQUIVALENT UNIFORM LOAD (psf) (to be added to floor dead and live loads)
50 or less | 0
51 to 100 | 6
101 to 200 | 12
201 to 350 | 20
Greater than 350 | 20 plus a concentrated live load of the weight in excess of 350 plf.

## 1607.11.1
TABLE 1607.11.1
LIVE LOAD ELEMENT FACTOR, KLL
ELEMENT | KLL
Interior columns Exterior columns without cantilever slabs | 4 4
Edge columns with cantilever slabs | 3
Corner columns with cantilever slabs Edge beams without cantilever slabs Interior beams | 2 2 2
All other members not identified above including: Edge beams with cantilever slabs Cantilever beams One-way slabs Two-way slabs Members without provisions for continuous shear transfer normal to their span | 1

## 1609.1.2
TABLE 1609.1.2
WIND-BORNE DEBRIS PROTECTION FASTENING SCHEDULE FOR WOOD STRUCTURAL PANELSa, b, c, d
FASTENER TYPE | FASTENER SPACING (inches)
| Panel Span ≤ 4 feet | 4 feet < Panel Span ≤ 6 feet | 6 feet < Panel Span ≤ 8 feet
No. 8 wood-screw-based anchor with 2-inch embedment length | 16 | 10 | 8
No. 10 wood-screw-based anchor with 2-inch embedment length | 16 | 12 | 9
1/4-inch diameter lag-screw-based anchor with 2-inch embedment length | 16 | 16 | 16

## 1609.3
TABLE 1609.3
BASIC DESIGN WIND SPEED
Risk Category | Basic Design Wind Speed, mph (3-sec gust, 33 ft. for Exposure Category C) | Mean Recurrence Interval, years | Probability of Exceedance in 50 years, %
I | 110 | 300 | 15
II | 117 | 700 | 7
III | 127 | 1700 | 3
IV | 132 | 3000 | 1.6

## 1609.3.2
TABLE 1609.3.2
SERVICEABILITY DESIGN WIND SPEED
Mean Recurrence Interval (years) | Serviceability Design Wind Speed, mph (3-sec gust, 33 ft. for Exposure Category C)
10 | 80
25 | 87
50 | 93
100 | 100

## 1609.7
TABLE 1609.7
NET PRESSURE COEFFICIENT, (GCpn) FOR ATTACHED CANOPIES ON BUILDINGS WITH H>60 FT
Net Pressure Coefficient (GCpn) | h/hc
| 2 | 3 | 6 | 12 | 18 | 24 | 30
Upward | -0.6 | -0.7 | -0.95 | -1.04 | -1.16 | -1.3 | -1.3
Downward | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9

## 1610.1
TABLE 1610.1
LATERAL SOIL LOAD
DESCRIPTION OF BACKFILL MATERIALc | UNIFIED SOIL CLASSIFICATION | DESIGN LATERAL SOIL LOADa (pound per square foot per foot of depth)
|  | Active pressure | At-rest pressure
Well-graded, clean gravels; gravel-sand mixes | GW | 30 | 60
Poorly graded clean gravels; gravel-sand mixes | GP | 30 | 60
Silty gravels, poorly graded gravel-sand mixes | GM | 40 | 60
Clayey gravels, poorly graded gravel-and-clay mixes | GC | 45 | 60
Well-graded, clean sands; gravelly sand mixes | SW | 30 | 60
Poorly graded clean sands; sand-gravel mixes | SP | 30 | 60
Silty sands, poorly graded sand-silt mixes | SM | 45 | 60
Sand-silt clay mix with plastic fines | SM-SC | 45 | 100
Clayey sands, poorly graded sand-clay mixes | SC | 60 | 100
Inorganic silts and clayey silts | ML | 45 | 100
Mixture of inorganic silt and clay | ML-CL | 60 | 100
Inorganic clays of low to medium plasticity | CL | 60 | 100
Organic silts and silt clays, low plasticity | OL | Note b | Note b
Inorganic clayey silts, elastic silts | MH | Note b | Note b
Inorganic clays of high plasticity | CH | Note b | Note b
Organic clays and silty clays | OH | Note b | Note b

## 1613.3.3(1)
TABLE 1613.3.3(1)
VALUES OF SITE COEFFICIENT Fa AS A FUNCTION OF SITE CLASS AND MAPPED SPECTRAL RESPONSE ACCELERATION AT SHORT PERIODS (SS)a
SITE CLASS | Fa
A | 0.8
B (Vs measured) | 0.9
B (Vs unmeasured) | 1
C | 1.3
D | 1.57
E | 2.28
F | Note a

## 1613.3.3(2)
TABLE 1613.3.3(2)
VALUES OF SITE COEFFICIENT Fv AS A FUNCTION OF SITE CLASS AND MAPPED SPECTRAL RESPONSE ACCELERATION AT 1-SECOND PERIOD (S1)a
SITE CLASS | Fv
A | 0.8
B (Vs measured) | 0.9
B (Vs unmeasured) | 1
C | 1.5
D | 2.4
E | 4.2
F | Note a

## 1613.3.4.1
TABLE 1613.3.4.1
SITE CLASSIFICATIONa
SITE CLASS | vs | N or Nch | su
E | < 600 ft/s | < 15 | < 1,000 psf
D | 600 to 1,200 ft/s | 15 to 50 | 1,000 to 2,000 psf
C | 1,200 to 2,500 ft/s | > 50 | > 2,000

## 1613.3.5
TABLE 1613.3.5
SEISMIC DESIGN CATEGORY
RISK CATEGORY | SITE CLASS
| A | B/C/D | E
I/II/III | A | B | C
IV | A | C | D

## 1613.5
TABLE 1613.5
DESIGN COEFFICIENT AND FACTORS FOR BASIC SEISMIC C-FORCE-RESISTING SYSTEMS
Seismic Force-Resisting System | ASCE 7 Section Where Detailing Requirements Are Specified | Response Modification Coefficient Ra | Overstrength Factor Ω0g | Deflection Amplification Factor Cdb | B | C | Dd
A. BEARING WALL SYSTEMS
1. Special reinforced concrete shear wallsl, m | 14.2 | 5 | 2.5 | 5 | NL | NL | 160
2. Ordinary reinforced concrete shear wallsl | 14.2 | 4 | 2.5 | 4 | NL | NL | NP
3. Detailed plain concrete shear wallsl | 14.2 | 2 | 2.5 | 2 | NL | NP | NP
4. Ordinary plain concrete shear wallsl | 14.2 | 1.5 | 2.5 | 1.5 | NL | NP | NP
5. Intermediate precast shear wallsl | 14.2 | 4 | 2.5 | 4 | NL | NL | 40k
6. Ordinary precast shear wallsl | 14.2 | 3 | 2.5 | 3 | NL | NP | NP
7. Special reinforced masonry shear walls | 14.4 | 5 | 2.5 | 3.5 | NL | NL | 160
8. Intermediate reinforced masonry shear walls | 14.4 | 3.5 | 2.5 | 2.25 | NL | NL | NP
9. Ordinary reinforced masonry shear walls | 14.4 | 2 | 2.5 | 1.75 | NL | 160 | NP
10. Detailed plain masonry shear walls | 14.4 | 2 | 2.5 | 1.75 | NL | NP | NP
11. Ordinary plain masonry shear walls | 14.4 | 1.5 | 2.5 | 1.25 | NL | NP | NP
12. Prestressed masonry shear walls | 14.4 | 1.5 | 2.5 | 1.75 | NL | NP | NP
13. Ordinary reinforced Autoclaved Aerated Concrete (AAC) masonry shear walls | 14.4 | 2 | 2.5 | 2 | NL | 35 | NP
14. Ordinary plain (unreinforced) Autoclaved Aerated Concrete (AAC) masonry shear walls | 14.4 | 1.5 | 2.5 | 1.5 | NL | NP | NP
15. Light-frame (wood) walls sheathed with wood structural panels rated for shear resistance or steel sheets | 14.1 and 14.5 | 6.5 | 3 | 4 | NL | NL | 65
16. Light-frame (cold-formed steel) walls sheathed with wood structural panels rated for shear resistance or steel sheets | 14.1 | 6.5 | 3 | 4 | NL | NL | 65
17. Light-frame walls with shear panels of all other materials | 14.1 and 14.5 | 2 | 2.5 | 2 | NL | NL | 35
18. Light-frame (cold-formed steel) wall systems using flat strap bracing | 14.1 | 4 | 2 | 3.5 | NL | NL | 65
B. BUILDING FRAME SYSTEMS
1. Steel eccentrically braced frames | 14.1 | 8 | 2 | 4 | NL | NL | 160
2. Steel special concentrically braced frames | 14.1 | 6 | 2 | 5 | NL | NL | 160
3. Steel ordinary concentrically braced frames | 14.1 | 3.25 | 2 | 3.25 | NL | NL | 35j
4. Special reinforced concrete shear wallsl, m | 14.2 | 6 | 2.5 | 5 | NL | NL | 160
5. Ordinary reinforced concrete shear wallsl | 14.2 | 5 | 2.5 | 4.5 | NL | NL | NP
6. Detailed plain concrete shear wallsl | 14.2 and 14.2.2.7 | 2 | 2.5 | 2 | NL | NP | NP
7. Ordinary plain concrete shear wallsl | 14.2 | 1.5 | 2.5 | 1.5 | NL | NP | NP
8. Intermediate precast shear wallsl | 14.2 | 5 | 2.5 | 4.5 | NL | NL | 40k
9. Ordinary precast shear wallsl | 14.2 | 4 | 2.5 | 4 | NL | NP | NP
10. Steel and concrete composite eccentrically braced frames | 14.3 | 8 | 2.5 | 4 | NL | NL | 160
11. Steel and concrete composite special concentrically braced frames | 14.3 | 5 | 2 | 4.5 | NL | NL | 160
12. Steel and concrete composite ordinary braced frames | 14.3 | 3 | 2 | 3 | NL | NL | NP
13. Steel and concrete composite plate shear walls | 14.3 | 6.5 | 2.5 | 5.5 | NL | NL | 160
14. Steel and concrete composite special shear walls | 14.3 | 6 | 2.5 | 5 | NL | NL | 160
15. Steel and concrete composite ordinary shear walls | 14.3 | 5 | 2.5 | 4.5 | NL | NL | NP
16. Special reinforced masonry shear walls | 14.4 | 5.5 | 2.5 | 4 | NL | NL | 160
17. Intermediate reinforced masonry shear walls | 14.4 | 4 | 2.5 | 4 | NL | NL | NP
18. Ordinary reinforced masonry shear walls | 14.4 | 2 | 2.5 | 2 | NL | 160 | NP
19. Detailed plain masonry shear walls | 14.4 | 2 | 2.5 | 2 | NL | NP | NP
20. Ordinary plain masonry shear walls | 14.4 | 1.5 | 2.5 | 1.25 | NL | NP | NP
21. Prestressed masonry shear walls | 14.4 | 1.5 | 2.5 | 1.75 | NL | NP | NP
22. Light-frame (wood) walls sheathed with wood structural panels rated for shear resistance | 14.5 | 7 | 2.5 | 4.5 | NL | NL | 65
23. Light-frame (cold-formed steel) walls sheathed with wood structural panels rated for shear resistance or steel sheets | 14.1 | 7 | 2.5 | 4.5 | NL | NL | 65
24. Light-frame walls with shear panels of all other materials | 14.1 and 14.5 | 2.5 | 2.5 | 2.5 | NL | NL | 35
25. Steel buckling-restrained braced frames | 14.1 | 8 | 2.5 | 5 | NL | NL | 160
26. Steel special plate shear walls | 14.1 | 7 | 2 | 6 | NL | NL | 160
C. MOMENT-RESISTING FRAME SYSTEMS
1. Steel special moment frames | 14.1 and 12.2.5.5 | 8 | 3 | 5.5 | NL | NL | NL
2. Steel special truss moment frames | 14.1 | 7 | 3 | 5.5 | NL | NL | 160
3. Steel intermediate moment frames | 14.1 and 12.2.5.7 | 4.5 | 3 | 4 | NL | NL | 35h
4. Steel ordinary steel moment frames | 14.1 and 12.2.5.6 | 3.5 | 3 | 3 | NL | NL | NPi
5. Special reinforced concrete moment framesn | 14.2 and 12.2.5.5 | 8 | 3 | 5.5 | NL | NL | NL
6. Intermediate reinforced concrete moment frames | 14.2 | 5 | 3 | 4.5 | NL | NL | NP
7. Ordinary reinforced concrete moment frames | 14.2 | 3 | 3 | 2.5 | NL | NP | NP
8. Steel and concrete composite special moment frames | 14.3 and 12.2.5.5 | 8 | 3 | 5.5 | NL | NL | NL
9. Steel and concrete composite intermediate moment frames | 14.3 | 5 | 3 | 4.5 | 160 | 160 | NP
10. Steel and concrete composite partially restrained moment frames | 14.3 | 6 | 3 | 5.5 | NL | NL | 100
11. Steel and concrete composite ordinary moment frames | 14.3 | 3 | 3 | 2.5 | NL | NP | NP
12. Cold-formed steel—special bolted moment framep | 14.1 | 3.5 | 3o | 3.5 | 35 | 35 | 35
D. DUAL SYSTEMS WITH SPECIAL MOMENT FRAMES CAPABLE OF RESISTING AT LEAST 25% OF PRESCRIBED SEISMIC FORCES | 12.2.5.1 | Ra | Ω0g | Cdb | B | C | Dd
1. Steel eccentrically braced frames | 14.1 | 8 | 2.5 | 4 | NL | NL | NL
2. Steel special concentrically braced frames | 14.1 | 7 | 2.5 | 5.5 | NL | NL | NL
3. Special reinforced concrete shear wallsl | 14.2 | 7 | 2.5 | 5.5 | NL | NL | NL
4. Ordinary reinforced concrete shear wallsl | 14.2 | 6 | 2.5 | 5 | NL | NL | NP
5. Steel and concrete composite eccentrically braced frames | 14.3 | 8 | 2.5 | 4 | NL | NL | NL
6. Steel and concrete composite special concentrically braced frames | 14.3 | 6 | 2.5 | 5 | NL | NL | NL
7. Steel and concrete composite plate shear walls | 14.3 | 7.5 | 2.5 | 6 | NL | NL | NL
8. Steel and concrete composite special shear walls | 14.3 | 7 | 2.5 | 6 | NL | NL | NL
9. Steel and concrete composite ordinary shear walls | 14.3 | 6 | 2.5 | 5 | NL | NL | NP
10. Special reinforced masonry shear walls | 14.4 | 5.5 | 3 | 5 | NL | NL | NL
11. Intermediate reinforced masonry shear walls | 14.4 | 4 | 3 | 3.5 | NL | NL | NP
12. Steel buckling-restrained braced frames | 14.1 | 8 | 2.5 | 5 | NL | NL | NL
13. Steel special plate shear walls | 14.1 | 8 | 2.5 | 6.5 | NL | NL | NL
E. DUAL SYSTEMS WITH INTERMEDIATE MOMENT FRAMES CAPABLE OF RESISTING AT LEAST 25% OF PRESCRIBED SEISMIC FORCES | 12.2.5.1 | Ra | Ω0g | Cdb | B | C | Dd
1. Steel special concentrically braced framesf | 14.1 | 6 | 2.5 | 5 | NL | NL | 35
2. Special reinforced concrete shear wallsl | 14.2 | 6.5 | 2.5 | 5 | NL | NL | 160
3. Ordinary reinforced masonry shear walls | 14.4 | 3 | 3 | 2.5 | NL | 160 | NP
4. Intermediate reinforced masonry shear walls | 14.4 | 3.5 | 3 | 3 | NL | NL | NP
5. Steel and concrete composite special concentrically braced frames | 14.3 | 5.5 | 2.5 | 4.5 | NL | NL | NL
6. Steel and concrete composite ordinary braced frames | 14.3 | 3.5 | 2.5 | 3 | NL | NL | NP
7. Steel and concrete composite ordinary shear walls | 14.3 | 5 | 3 | 4.5 | NL | NL | NP
8. Ordinary reinforced concrete shear wallsl | 14.2 | 5.5 | 2.5 | 4.5 | NL | NL | NP
F. SHEAR WALL-FRAME INTERACTIVE SYSTEM WITH ORDINARY REINFORCED CONCRETE MOMENT FRAMES AND ORDINARY REINFORCED CONCRETE SHEAR WALLSl | 14.2 and 12.2.5.8 | 4.5 | 2.5 | 4 | NL | NP | NP
G. CANTILEVERED COLUMN SYSTEMS DETAILED TO CONFORM TO THE REQUIREMENTS FOR: | 12.2.5.2 | Ra | Ω0g | Cdb | B | C | Dd
1. Steel special cantilever column systems | 14.1 | 2.5 | 1.25 | 2.5 | 35 | 35 | 35
2. Steel ordinary cantilever column systems | 14.1 | 1.25 | 1.25 | 1.25 | 35 | 35 | NPi
3. Special reinforced concrete moment framesn | 14.2 and 12.2.5.5 | 2.5 | 1.25 | 2.5 | 35 | 35 | 35
4. Intermediate reinforced concrete moment frames | 14.2 | 1.5 | 1.25 | 1.5 | 35 | 35 | NP
5. Ordinary reinforced concrete moment frames | 14.2 | 1 | 1.25 | 1 | 35 | NP | NP
6. Timber frames | 14.5 | 1.5 | 1.5 | 1.5 | 35 | 35 | 35
H. STEEL SYSTEMS NOT SPECIFICALLY DETAILED FOR SEISMIC RESISTANCE, EXCLUDING CANTILEVER COLUMN SYSTEMS | 14.1 | 3 | 3 | 3 | NL | NL | NP

## 1705.2
TABLE 1705.2
‡‡‡ REQUIRED SPECIAL INSPECTION OF STEEL CONSTRUCTION
TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARDa | BC REFERENCE
1. Material verification of high-strength bolts, nuts and washers:
a. Identification markings to conform to ASTM standards specified in the approved construction documents. | — | X | AISC 360, Section A3.3; applicable ASTM material specifications; and RCSC Specification for Structural Joints Using High-Strength Bolts Section 2 | —
b. Manufacturer's certificate of compliance required. | — | X | RCSC Specification for Structural Joints Using High-Strength Bolts Section 2.1 | —
2. Inspection of high-strength bolting:
a. Snug-tight joints. | — | X
b. Pre-tensioned and slip-critical joints using turn-of-nut with matchmarking, twist-off bolt or direct tension indicator methods of installation. | — | X | AISC 360 Section M2.5; and RCSC Specification for Structural Joints Using High-Strength Bolts Section 9 | 1705.2.3
c. Pre-tensioned and slip-critical joints using turn-of-nut without matchmarking or calibrated wrench methods of installation. | X | —
d. Pre-installation verification testing. | X | — | Specification for Structural Joints Using High-Strength Bolts Section 8.2 | 1705.2.3.1
3. Material verification of structural steel and cold formed steel deck:
a. For structural steel, identification markings to conform to AISC 360. | — | X | AISC 360 Sections A3.1, N2.1, N3.2 (a) and (k)(1) | —
b. For other steel, identification markings to conform to ASTM standards specified in the approved construction documents. | — | — | Applicable ASTM Standards | —
c. Manufacturers' certified mill test reports. | — | X | Applicable ASTM material standards | —
4. Material verification of weld filler materials:
a. Identification markings to conform to AWS specification in the approved construction documents. | — | — | AISC 360 Section A3.5 and N3.2(e), and applicable AWS A5 documents; and AWS D1.1 5.3.1 and approved contract documents | —
b. Manufacturer's certificate of compliance required. | — | — | AISC 360 Section A3.5 | —
5. Inspection of welding:
a. Structural steel: | — | — | — | —
1) Complete and partial penetration groove welds. | X | — | AWS D1.1 | 1705.2.1
2) Multipass fillet welds. | X | — | AWS D1.1 | 1705.2.1
3) Single-pass fillet welds > 5/16". | X | — | AWS D1.1 | 1705.2.1
4) Plug and slot welds. | X | — | AWS D1.1 | 1705.2.1
5) Single-pass fillet welds ≤ 5/16". | — | X | AWS D1.1 | 1705.2.1
6) Floor and roof deck welds. | — | X | AWS D1.3 | —
7) Cold-formed steel welds. | — | X | AWS D1.3 | —
b. Reinforcing steel: | — | —
1) Pre-welding verification of base metal. | — | X | AWS D1.4 | 1903.6.2
2) Reinforcing steel resisting flexural and axial forces in intermediate and special moment frames, and boundary elements of special reinforced concrete shear walls and shear reinforcement. | X | — | AWS D1.4 | 1903.6.2
3) Shear reinforcement. | X Note a | — | AWS D1.4 | 1903.6.2
4) Other reinforcing steel. | — | X Note b | AWS D1.4 | 1903.6.2
6. Inspection of steel frame joint details for compliance with approved construction documents:
a. Details such as bracing and stiffening. | — | X | — | 1705.2.2
b. Member locations. | — | X
c. Application of joint details at each connection. | — | X

## 1705.2.6
TABLE 1705.2.6
‡‡‡ REQUIRED SPECIAL INSPECTION OF COLD-FORMED STEEL CONSTRUCTION
TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC REFERENCE
1. Material Verification:
a. Verify that identification markings conform to AISI S240 and as specified in the approved construction documents. | X |  | AISI S240, Section D6.5
b. Verify that material is clean, straight and undamaged. |  | X
2. Inspection of general framing:
a. Verify that member sizes conform to the approved construction documents. |  | X | AISI S240 Section C
b. Verify that member layout conforms to the approved construction documents. |  | X | AISI S240 Section C
c. Verify that proper bearing lengths are provided in accordance with approved construction documents. |  | X | AISI S240 Section C
d. Verify that punched holes and sheared or flame cut edges of material in members are clean and free from notches and burred edges. |  | X | AISI S240 Section C
3. Inspection of framing connections and anchorages:
a. Verify that screws, bolts, and other fasteners conform to approved construction document requirements for diameter, length, quantity, spacing, edge distance, and location. |  | X | AISI S240, Section D6.7
b. Verify that manufactured connectors, such as joist hangers, caps, straps, clips, ties, hold-downs, and anchors conform to approved construction document requirements for manufacturer, type, gauge, and fastener requirements. |  | X | AISI S240 Section B1.5 and Section C4
c. Post-installed connections to concrete. | X |  | AISI S240 Section D6.9
4. Inspection of welding:
a. Inspect welds in accordance with S240 Section D6.6. |  | X | AWS D1.3, AISI S240 Section D6.6
b. Additional requirements for welds performed as a part of a lateral force-resisting system. | X Note a |  | AISI S240 Section D6.9
5. Bracing:
a. Verify that temporary bracing, shoring, jacks, etc., are installed, modified and not removed until no longer necessary, in accordance with the approved construction documents and approved erection drawings as required by Sections 3305.8.6.8 and 3305.8.7.5. |  | X | AISI S240 Section E6
b. Verify that permanent bracing, web stiffeners, bridging, blocking, wind bracing, etc., are installed in accordance with the approved construction documents and approved erection drawings, as required by Sections 3305.8.6.8 and 3305.8.7.5. |  | X | AISI S240 Section E6
c. Where a cold-formed steel truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package. |  | X | AISI S240 Section E6 | 2211.1.3.2
6. Pre-installation Document Submittals |  | X | AISI S240, Section D3
7. Lateral Force-Resisting System Additional Requirements |  | X | AISI S240 Section D6.9

## 1705.2.7
TABLE 1705.2.7
REQUIRED SPECIAL INSPECTIONS OF OPEN-WEB STEEL JOISTS AND JOIST GIRDERS
TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC REFERENCE
1. Inspection of member sizes and locations. | — | X
2. Inspection of end connections – welded or bolted | — | X | SJI Specifications | 2207.1
3. Inspection of standard bridging, horizontal or diagonal | — | X | SJI Specifications | 2207.1
4. Inspection of bridging, horizontal or diagonal, that differs from the SJI specifications listed in Section 2207.1 | — | X | SJI Specifications

## 1705.3
TABLE 1705.3
‡‡‡ REQUIRED SPECIAL INSPECTIONS AND TESTS OF CONCRETE CONSTRUCTION
TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC REFERENCE | CONCRETE SPECIAL INSPECTOR (CAST-IN-PLACE, PRECAST, & PRESTRESSED) | LICENSED CONCRETE TESTING LABORATORY
1. Inspect reinforcement, including prestressing tendons and verify placement. | — | X | ACI 318: 3.5, 7.1 – 7.7 | 1903.6, 1907.1, 1907.7, 1911.4 | X
2. Inspection of reinforcing steel welding in accordance with Table 1705.2, Item 5b. | — | — | AWS D1.4 ACI 318: 3.5.2 | 1903.6.2
3. Inspect anchors cast in concrete. | X | — | ACI 318: 17.8.2 | 1901.3 | X
4. Inspect anchors post-installed in hardened concrete membersc.
a. Adhesive anchors installed in horizontally or upwardly inclined orientations to resist sustained tension loads. | X | — | ACI 318: 17.8 |  | X
b. Mechanical anchors and adhesive anchors not defined in 4a. | — | X
5. Verifying use of required design mix. | — | — | ACI 318: Ch. 4, 5.2–5.4 | 1904, 1905.2–1905.4, 1911.3 |  | X
6. Prior to concrete placement, fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of the concrete. Determine water content when required. | — | — | ASTM C 172 ASTM C 31 ACI 318: 5.6, 5.8 (Notes a, b) | 1905.6, 1911.10 |  | X
7
a. Inspect concrete and shotcrete placement for proper application techniques. | X | — | ACI 318: 5.9, 5.10 | 1905.9, 1905.10, 1911.6, | X
b. For concrete pumped through a placement boom: Following the lubrication of the concrete placement boom and prior to Contractor's commencement of the concrete pour, observe and document as part of the special inspection of the concrete placement whether the material exiting the hose is concrete exhibiting a uniform matrix of aggregate. |  |  |  | 1911.7, 1911.8
8. Verify maintenance of specified curing temperature and techniques. Monitoring of in-place temperatures per thermal protection plan when required. | — | X | ACI 318: 5.11–5.13 | 1905.11, 1905.13, 1911.9 | X
9. Inspect prestressed concrete for:
A. Application of prestressing forces; and | X | — | ACI 318: 18.20 ACI 318: 18.18.4 | — | X
B. Grouting of bonded prestressing tendons. | X | —
10. Inspect erection of precast concrete members. | — | X | ACI 318: Ch. 16 | — | X
11. Verify in-situ concrete strength, prior to stressing of tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | — | X | ACI 318: 6.2 | 1906.2 | — | X
12. Inspect formwork for shape, location, and dimensions of the concrete member being formed. | — | X | ACI 318: 6.1.1 | 1906.2 | X

## 1705.4.1
TABLE 1705.4.1
LEVEL 2† REQUIRED SPECIAL INSPECTIONS AND TESTS OF MASONRY CONSTRUCTION
MINIMUM TESTS
Verification of Slump flow and Visual Stability Index (VSI) as delivered to the project site in accordance with TMS 602 Article 1.5.B.1.b.3 for self-Consolidating grout.
Verification of f'm and f'AAC in accordance with TMS 602 Article 1.4 B prior to construction, except where specifically exempted by this Code.
TYPE | Continuous Special Inspection | Periodic Special Inspection | BC Section | TMS 402 | TMS 602
1. Verify compliance with required inspection provisions of the construction documents and the approved submittals. | — | X | — | — | Art. 1.5
2. As masonry construction begins, the following shall be verified to ensure compliance:
a. Proportions of site-prepared mortar. | — | X | — | — | Art. 2.6A
b. Construction of mortar joints. | — | X | — | — | Art. 3.3B
c. Grade and size of prestressing tendons and anchorages. | — | X | — | — | Art. 2.4B, 2.4H
d. Location of reinforcement, connectors, prestressing tendons and anchorages. | — | X | — | — | Art. 3.4, 3.6A
e. Prestressing technique. | — | X | — | — | Art. 3.6B
3. Prior to grouting, the following shall be verified to ensure compliance:
a. Grout space. | — | X | — | — | Art. 3.2D
b. Grade, type, and size of reinforcement and anchor bolts, and prestressing tendons and anchorages. | — | X | — | — | —
c. Placement of reinforcement, connectors, and prestressing tendons and anchorages. | — | X | — | Sec. 1.13 | Art. 3.4
d. Proportions of site-prepared grout and prestressing grout for bonded tendons. | — | X | — | — | Art. 2.6B
e. Construction of mortar joints. | — | X | — | — | Art. 3.3B
4. Verify during construction:
a. Size and location of structural elements. | — | X | — | — | Art. 3.3F
b. Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction. | — | X | — | Sec. 1.2.1(e), 14.4.3 | —
c. Welding of reinforcement. | X | — | — | Sec. 1.2.1(g), 6.1.6.1.2, 6.1.7.3, 13.7 | —
d. Preparation, construction and protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F). | — | X | Sec. 2104.2, 2104.3 | Sec 3.1.3 | Art. 1.8C, 1.8D
e. Preparation of any required grout specimens, mortar specimens and/or prisms shall be observed. | — | X | — | Art. 3.1.3 | Art. 1.4
f. Application and measurement of prestressing force. | X | — | — | — | Art. 3.6B
g. Placement of grout and prestressing grout for bonded tendons is in compliance. | X | — | — | — | Art. 3.5, 3.6 C
h. Placement of AAC masonry units and construction of thin-bed mortar joints. | Xb | Xc | — | — | Art. 3.3 B.9, 3.3 F.1.b
i. Grout space is clean. | — | X | — | — | Art. 3.2D
j. Placement of reinforcement and connectors, and prestressing tendons and anchorages. | — | X | — | Sec. 6.1.3 and 10.8 | Art. 3.4
k. Proportions of site-prepared grout and prestressing grout for bonded tendons. | — | X | — | — | Art. 2.6B
l. Construction of mortar joints. | — | X | — | — | Art. 3.3B
5. Observe preparation of grout specimen, mortar specimen, and/or prisms. | — | X | — | — | Art. 1.4B2a3, 1.4B2b3, 1.4B2c3, 1.4B3, 1.4B4, 2.1A

## 1705.4.3
TABLE 1705.4.3
‡‡‡ LEVEL 3† REQUIRED SPECIAL INSPECTIONS AND TESTS OF MASONRY CONSTRUCTION
MINIMUM TESTS
Verification of f'm and f'AAC in accordance with TMS 602 Article 1.4 B prior to construction and every 5,000 sq. ft. during construction.
Verification of proportions of materials in premixed or preblended mortar, prestressing grout, and grout other than self-consolidating grout, as delivered to the project site in accordance with TMS 602 Article 1.5B.
Verification of Slump flow and Visual Stability Index (VSI) as delivered to the project site in accordance with TMS 602 Article 1.5.B.1.b.3 for self-consolidating grout.
MINIMUM SPECIAL INSPECTION
TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | BC Section | TMS 402 | TMS 602a
1. Verify compliance with required inspection provisions of the construction documents and the approved submittals. | — | X | — | — | Art. 1.5
2. Verify that the following are in compliance:
a. Proportions of site-prepared mortar, grout and prestressing grout for bonded tendons. | — | X | — | — | Art. 2.6 A
b. Grade, type, and size of reinforcement and anchor bolts, and prestressing grout for bonded tendons. | — | X‡ | — | Sec. 6.1.2, 10.8 | Art. 2.4, 3.4
c. Placement of masonry units and construction of mortar joints. | —‡ | X | — | — | Art. 3.3 B
d. Placement of reinforcement, connectors and prestressing tendons and anchorages. | — | X | — | Sec. 6.1.2, 10.8 | Art. 3.4, 3.6 A
e. Grout space prior to grouting. | X | — | — | — | Art. 3.2 D
f. Placement of grout and prestressing grout for bonded tendons. | X | — | — | — | Art. 3.5
g. Placement of prestressing grout. | X | — | — | — | Art. 3.6 C
h. Size and location of structural elements. | — | X | — | — | Art. 3.3 F
i. Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction. | X | — | — | Sec. 1.2.1(e), 14.4.3 | —
j. Welding of reinforcement. | X | — | — | Sec. 1.2.1(g), 6.1.6.1.2, 6.1.7.3, 13.7 | —
k. Preparation, construction and protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F). | — | X | Sec. 2104.2, 2104.3 | — | Art. 1.8 C, 1.8 D
l. Application and measurement of prestressing force. | X | — | — | — | Art. 3.6 B
m. Placement of AAC masonry units and construction of thin-bed mortar joints. | X | — | — | — | Art. 3.3 B.9, 3.3 F.1.b
n. Properties of thin-bed mortar for AAC masonry. | X | — | — | — | Art. 2.1 C.1
6. Observe preparation of grout specimens, mortar specimens, and/or prisms. | X | — | — | Sec. 3.1.3 | Art. 1.4

## 1705.5.6
TABLE 1705.5.6
‡‡‡ REQUIRED SPECIAL INSPECTIONS OF TYPE IV CONSTRUCTION UTILIZING CROSS-LAMINATED TIMBER OR STRUCTURAL COMPOSITE LUMBER
TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC‡ CODE REFERENCE
1. Inspection of anchorage and connections of mass timber construction to timber deep foundation systems | — | X |  | 1705.7, 2308.3, 2304.10
2. Inspect erection of mass timber, including material verification | — | X | PRG-320, ASTM D5456 | 2303.1.4, 2303.1.10
3. Inspection of connections where installation methods are required to meet design loads
3.1. Threaded fasteners | — | X
3.1.1. Verify use of proper installation equipment | — | X | NDS 11-14 ANSI/ASME Standard B18.2.1, B18.6.1 As per connection manufacturer's installation instructions | 2304.10, 2304.11.1.1 to 2304.11.4
3.1.2. Verify use of pre-drilled holes where required | — | X
3.1.3. Inspect screws, including diameter, length, head type, spacing, installation angle, and depth | — | X
3.2. Adhesive anchors installed in horizontal or upwardly inclined orientation to resist sustained tension loads | X | —
3.3. Adhesive anchors not defined in 3.2 | — | X
3.4. Bolted connections | — | X
3.5. Concealed connections | — | X
3.6. Other fastener types | — | X
4. Inspection of connections where installation methods are required to meet the fire resistance design in Section‡ 2304.10.8 | — | X | NDS 16.3

## 1705.6
TABLE 1705.6
REQUIRED SPECIAL INSPECTIONS OF SUBSURFACE CONDITIONS
TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION
1. Special inspection of subsurface investigations, borings and test pits. Boring and test pit operations, and alternative investigation methods, shall be subject to continuous special inspection to verify compliance with Section 1803. Soil sample recovery operations for test pits shall be subject to continuous special inspection to verify compliance with Section 1803. Exceptions: 1. Cone penetrometer testing used as an alternative investigation method per Section 1803.5.2 shall be subject to periodic special inspection. 2. Existing boring, test pit and alternative investigation records that have been deemed acceptable to the commissioner in accordance with Section 1803.4.2 are not subject to special inspection. | X | —
2. During fill placement. During placement and compaction of the fill material, the special inspector shall determine that the material being used and the maximum lift thickness comply with the approved geotechnical report, as specified in Section 1804.6‡. | X | —
3. Evaluation of in-place density. The special inspector shall determine that the in-place dry density of the compacted fill complies with the approved construction documents. | X | —
4. Subgrade inspection. Immediately prior to placement of each and every footing, foundation, fill or other supporting materials, the special inspector shall determine that the site has been prepared and is in accordance with the approved geotechnical report. | — | X

## 1705.7
TABLE 1705.7
REQUIRED SPECIAL INSPECTIONS AND TESTS OF DEEP FOUNDATION ELEMENTS
INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION
1. Verify the identifying designation of the deep foundation element and record the date of installation, including the start and end times. | X | —
2. Verify the size, material, and allowable capacity as specified in the construction documents. | X | —
3. Record the elevation of the minimum required depth of penetration and record the final tip elevation and butt elevation. | X | —
4. Record the elevation of splices and note whether or not the splices were installed and located in compliance with the construction documents. | X | —
LOAD TEST
5. For load test requiring a load or reaction frame, inspect the construction of the load or reaction frame. Record the results of the inspection and note whether or not the frame complies with the construction documents prepared by the registered design professional. | — | X
6. Record the identifying designation for the element being tested, and the date of the testing, including the start and end time. | X | —
7. Record the method of performing the test, including the equipment being used, as well as the test results, noting whether or not the method of testing and the test results comply with the requirements of Sections 1810, 1811, and 1812 and the construction documents. | X | —

## 1705.7.1
TABLE 1705.7.1
REQUIRED SPECIAL INSPECTIONS OF DRIVEN AND VIBRATED DEEP FOUNDATION ELEMENTS
INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION
1. For driven deep foundation elements, record the type and size of hammer and record the number of blows per foot of penetration from the start of driving until the final blow count required by the construction documents is reached. | X | —
2. For vibrated deep foundation elements, record the equipment and method used for installation and record the time for each foot of penetration from the start of installation until completion. | X | —

## 1705.7.2
TABLE 1705.7.2
REQUIRED SPECIAL INSPECTIONS OF DRILLED DEEP FOUNDATION ELEMENTS
INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION
1. Record the equipment and method used for installation and record the time for each foot of penetration from the start of installation until completion. | X | —
2. For deep foundation elements requiring a rock socket: 2.1. Record the equipment and method of drilling the rock socket. Record the top elevation and bottom elevation of rock socket, as well as the time for each foot of drilling the rock socket. 2.2. Inspect the rock socket to verify rock quality as required by Section 1812 and the construction documents. Record the results of the inspection and note whether or not the rock socket complies with the requirements of Section 1812. | X | —

## 1705.7.3
TABLE 1705.7.3
REQUIRED SPECIAL INSPECTIONS OF DRIVEN OR DRILLED CAST-IN-PLACE DEEP FOUNDATION ELEMENTS
INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION
1. Prior to placing concrete, inspect the inside of the pile for alignment and damage. Record the results of the inspection, noting whether or not the pile is in compliance with Section 1812 and the construction documents. | X | —
2. Witness the placement of concrete or grout inside the deep foundation element, and record the volume placed. Note the date and time of placement, and whether or not the concrete or grout was placed in compliance with Section 1812 and the construction documents. | X | —

## 1705.8.1
TABLE 1705.8.1
REQUIRED SPECIAL INSPECTIONS OF PRESTRESSED SOIL AND ROCK ANCHORS
INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION
1. Special inspection of Casing Installation. Special inspector shall observe casing installation and confirm that anchors are installed through a fully cased borehole or installed through stable rock in an open hole drill hole. | X | —
2. Special inspection of Anchor Materials. Special inspector shall confirm that the materials used in prestressed rock and soil anchors conform Section 1815.3 and approved construction documents. Inspector shall confirm that bar tendons conform to ASTM A722 and that strand tendons conform to ASTM A416 or A882. | X | —
3. Special inspection of Anchor Installation. Special inspector shall confirm the preparation and installation of each anchor, including placement, type, size and location of anchors, accessories, corrosion protection and grout conforms to PTI DC35.1-4 and the approved construction documents. | X | —
4. Special inspection of Grout. At the time of grout placement, special inspector shall prepare 3" diameter grout cylinders at the intervals specified in Section 1812.1.1.2.1. Cylinders shall be prepared in accordance with ASTM C31/C31M. | X | —
5. Special inspection of Grout. At the time of grout placement, special inspector shall determine the specific gravity of grout in accordance with American Petroleum Institute (API) Recommended Practice 13B-1 or in accordance with ASTM C138. | X | —
6. Special inspection of Grout. The compressive strength of grout cylinders shall be verified using 3" diameter cylinders tested in accordance with ASTM C39 and Section 1812.1.1.2.2. | X | —
7. Special inspection of Load Test. The special inspector shall observe load testing of each anchor and confirm that the test is accordance with PTI DC35.1-14 (Sections 8.1 – 8.9) and Section 1815.5. Inspector shall confirm that testing lock-off, and test loads comply with approved construction documents and PTI DC35.1–14 (Sections 8.1 – 8.9). | X | —

## 1705.37
TABLE 1705.37
REQUIRED VERIFICATION AND INSPECTION OF POST-INSTALLED ANCHORS
TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC REFERENCE
1. Preparation, placement, type, size and location of anchors, including other details of anchors, installed in hardened concrete, and installed to hardened concrete and to another construction. |  |  |  | 1901.1
a. Adhesive anchors installed horizontally or upwardly inclined orientations to resist sustained tension loads. | X | — | ACI 318 17.8.2.4, ACI 318-11 D.9.2.4 | 1901.1
b. Mechanical anchors and adhesive anchors not defined in 1.a. | — | X | ACI 318 17.9.2 | 1901.1
2. Preparation, placement, type, size and location of anchors, including other details of anchors, installed in masonry, and installed to masonry and to another construction. | — | X | Manufacturer's specifications and installation instructions | Applicable department procedures
3. Preparation, placement, type, size and location of anchors, including other details of anchors, installed in stone, and installed to stone and to another construction. | — | X | Manufacturer's specifications and installation instructions

## 1806.1
TABLE 1806.1
ALLOWABLE BEARING PRESSURES
CLASS OF MATERIALS (Notes 1 and 3) | MAXIMUM ALLOWABLE BEARING PRESSURE (TSF) | MAXIMUM ALLOWABLE BEARING PRESSURE (kPa)
1. Bedrock (Notes 2 and 7)
1a Hard sound rock | 60 | 5746
1b Medium rock | 40 | 3830
1c Intermediate rock | 20 | 1915
1d Soft rock | 8 | 766
2. Sandy gravel and gravel (GW, GP) (Notes 4, 8, and 9)
2a Dense | 10 | 958
2b Medium | 6 | 575
3. Granular soils (GC, GM, SW, SP, SM, and SC) (Notes 4, 5, 8, and 9)
3a Dense | 6 | 575
3b Medium | 3 | 287
4. Clays (SC, CL, and CH) (Notes 4, 6, 8, and 9)
4a Hard | 5 | 479
4b Stiff | 3 | 287
4c Medium | 2 | 192
5. Silts and silty soils (ML and MH) (Notes 4, 8, and 9)
5a Dense | 3 | 287
5b Medium | 1.5 | 144
6. Nominally Unsatisfactory Bearing Materials: Loose granular soils Soft clay soils Loose silt All organic silts, organic clay, peats, soft clays, granular soils and varved silts | See 1806.2.1 | See 1806.2.1
7. Controlled and uncontrolled fills | See 1806.2.2 or 1806.2.3 | See 1806.2.2 or 1806.2.3

## 1810.2.13
TABLE 1810.2.13
MINIMUM CONCRETE COVER FOR CAST IN PLACE AND PRECAST CONCRETE PILESa
FOUNDATION ELEMENT OR CONDITION | MINIMUM COVER
1. Precast nonprestressed deep foundation elements Exposed to seawater Not manufactured under plant conditions Manufactured under plant control conditions | 3 inches 2 inches In accordance with Section 20.6.1.3.3 of ACI 318
2. Precast prestressed deep foundation elements Exposed to seawater Other | 2.5 inches In accordance with Section 20.6.1.3.3 of ACI 318
3. Cast-in-place deep foundation elements not enclosed by a steel pipe, tube or permanent casing | 2.5 inches
4. Cast-in-place deep foundation elements enclosed by a steel pipe, tube or permanent casing | 1 inch
5. Structural steel core within a steel pipe, tube or permanent casing | 2 inches
6. Cast-in-place drilled shafts enclosed by a stable rock socket | 1.5 inches

## 1810.4.1.3
TABLE 1810.4.1.3
BASIC MAXIMUM ALLOWABLE PILE LOADS
TYPE OF PILE | MAXIMUM ALLOWABLE PILE LOAD (TONS)
Caisson Piles | No upper limit
Open-end pipe (or tube) piles bearing on rock of Class 1a, 1b, or 1c | 18-in O.D. and greater: 250 14-in to 18-in O.D.: 200 12-in to 14-in O.D.: 150 10-in to 12-in O.D.: 100 8-in to 10-in O.D.: 60
Closed-end pipe (or tube) piles, H-piles, cast-in-place concrete, enlarged base piles, and precast concrete piles bearing on rock of Class 1a, 1b, or 1c | 150
Piles (other than timber or helical piles) bearing on soft rock of Class 1d | 80
Piles (other than timber or helical piles) that receive their principal support other than by direct bearing on rock of Class 1a through 1d | 75
Timber piles bearing on rock of Class 1a through 1d | 25
Timber piles bearing in suitable soils | 40 tons maximum permissible with load test, 30 tons maximum without load test.
Helical piles | 30 tons maximum permissible

## 1810.8
TABLE 1810.8
ALLOWABLE AXIAL STRESSES FOR MATERIALS USED IN DEEP FOUNDATION ELEMENTSa
MATERIAL TYPE AND CONDITION | MAXIMUM ALLOWABLE STRESSb
1. Concrete or grout in compressionc Cast-in-place with a permanent casing in accordance with Section 1812.5.2 Cast-in-place in a pipe, tube, other permanent casing or rock Cast-in-place without a permanent casing Precast nonprestressed Precast prestressed | 0.4 f'c 0.33 f'c 0.3 f'c 0.33 f'c 0.33 f'c - 0.27 fpc
2. Nonprestressed reinforcement in compression | 0.4 fy ≤ 30,000 psi
3. Structural steel in compression Cores within concrete-filled pipes or tubes Pipes, tubes or H-piles, where justified in accordance with Section 1810.4.1.5.1 Pipes or tubes for micropiles or caissons less than 14 inches in diameter Other pipes, tubes or H-piles Helical piles | 0.5 Fy ≤ 32,000 psi 0.5 Fy ≤ 32,000 psi 0.4 Fy ≤ 32,000 psi 0.35 Fy ≤ 16,000 psi 0.6Fy ≤ 0.5Fu
4. Nonprestressed reinforcement in tension Within micropiles or caissons less than 14 inches in diameter Other conditions | 0.6 fy 0.5 fy ≤ 24,000 psi
5. Steel in tension Structural steel cores in caisson piles Pipes, tubes or H-piles, where justified in accordance with Section 1810.4.1.5.1 Other pipes, tubes or H-piles Helical piles | 0.5 Fy ≤ 32,000 psi 0.5 Fy ≤ 32,000 psi 0.35 Fy ≤ 16,000 psi 0.6 Fy ≤ 0.5Fu
6. Timber | See Section 1811.5.4

## 1811.3(a)
TABLE 1811.3(a)
MINIMUM DRIVING RESISTANCE AND MINIMUM HAMMER ENERGY FOR STEEL H-PILES, PIPE PILES, PRECAST AND CAST-IN-PLACE CONCRETE PILES AND COMPOSITE PILES (other than timber)
MINIMUM DRIVING RESISTANCEa, c, d, e
Pile Capacity (tons) | Hammer Energyb (ft. lbs.) | Friction Piles (blows/ft.) | Piles Bearing on Soft Rock (Class 1d) (blows/ft.) | Piles Bearing on Rock (Class 1a, 1b, and 1c)
Up to 20 | 15000 | 19 | 48 | 5 Blows per 1/4 inch (Minimum hammer energy of 15,000 ft. lbs.)
| 19000 | 15 | 27
| 24000 | 11 | 16
30 | 15000 | 30 | 72
| 19000 | 23 | 40
| 24000 | 18 | 26
40 | 15000 | 44 | 96
| 19000 | 32 | 53
| 24000 | 24 | 34
> 40 | AS PER SECTION 1811.3

## 1811.3(b)
TABLE 1811.3(b)
MINIMUM DRIVING RESISTANCE AND HAMMER ENERGY FOR TIMBER PILES
PILE CAPACITY (TONS) | MINIMUM DRIVING RESISTANCE (BLOWS/in.) TO BE ADDED TO DRIVING RESISTANCE EXERTED BY NONBEARING MATERIALS (NOTES 1, 3, 4) | HAMMER ENERGY (ft./lbs.) (Note 2)
Up to 20 | Formula in Note 4 shall apply | 7,500–12,000
Over 20 to 25 |  | 9,000–12,000
14,000–16,000
Over 25 to 30 |  | 12,000–16,000 (single-acting hammers)
Greater than 30 |  | 15,000–20,000 (double-acting hammers)

## 1816.2.1
TABLE 1816.2.1
VALUES OF MAXIMUM CONSIDERED EARTHQUAKE MEAN (MCEG) PEAK GROUND ACCELERATIONS ADJUSTED FOR SITE CLASS EFFECTS, PGAM
SITE CLASS | PGAM(g)
A | 0.15
B (m) | 0.17
B (un-m) | 0.18
C | 0.22
D | 0.26
E | 0.36

## 1904.3
TABLE 1904.3
MINIMUM SPECIFIED COMPRESSIVE STRENGTH (f'c)
TYPE OR LOCATION OF CONCRETE CONSTRUCTION | MINIMUM SPECIFIED COMPRESSIVE STRENGTH (f'c at 28 days, psi)
Basement walls, foundation walls, exterior walls and other vertical concrete surfaces, basement slabs, interior slabs on grade except for garage floor slabs, and foundations not exposed to the weather | 3,000a
Driveways, curbs, walks, patios, porches, carport slabs, steps and other flatwork exposed to the weather, and garage floor slabs | 3,500b
Structural concrete exposed to weather | 4500

## 1904.4.2
TABLE 1904.4.2
REQUIREMENTS FOR CONCRETE EXPOSED TO DEICING CHEMICALS
CEMENTITIOUS MATERIALS | MAXIMUM PERCENT OF TOTAL CEMENTITIOUS MATERIALS BY WEIGHTa, b
Fly ash or other pozzolans conforming to ASTM C 618 | 25d
Slag conforming to ASTM C 989 | 50
Silica fume conforming to ASTM C 1240 | 10
Total of fly ash or other pozzolans, slag and silica fume | 50c
Total of fly ash or other pozzolans and silica fume | 35c

## 2103.2.3
TABLE 2103.2.3
CERAMIC TILE MORTAR COMPOSITIONS
LOCATION | MORTAR | COMPOSITION
Walls | Scratchcoat | 1 cement; 1/5 hydrated lime; 4 dry or 5 damp sand
| Setting bed and leveling coat | 1 cement; 1/2 hydrated lime; 5 damp sand to 1 cement 1 hydrated lime, 7 damp sand
Floors | Setting bed | 1 cement; 1/10 hydrated lime; 5 dry or 6 damp sand; or 1 cement; 5 dry or 6 damp sand
Ceilings | Scratchcoat and sand bed | 1 cement; 1/2 hydrated lime; 2 1/2 dry sand or 3 damp sand

## 2109.2.1
TABLE 2109.2.1
ALLOWABLE STRESS GROSS CROSS-SECTIONAL AREA FOR DRY-STACKED, SURFACE-BONDED CONCRETE MASONRY WALLS
DESCRIPTION | MAXIMUM ALLOWABLE STRESS (psi)
Compression standard block | 45
Flexural tension
Horizontal span | 30
Vertical span | 18
Shear | 10

## 2109.4.3
TABLE 2109.4.3
MINIMUM THICKNESS OF MASONRY PARTITIONS
HEIGHT OF WALLS | THICKNESS
8 ft. and under | 2 in.
Over 8 ft. to 12 ft | 3 in.
Over 12 ft. to 16 ft | 4 in.
Over 16 ft. to 20 ft | 6 in.
Over 20 ft. to 24 ft. | 8 in.

## 2111.1
TABLE 2111.1
REQUIREMENTS FOR MASONRY FIREPLACES AND CHIMNEYSa
ITEM | LETTER | SECTION
Hearth and hearth extension thickness | A | 2111.1
Hearth extension (each side of opening) | B | 2111.11
Hearth extension (front of opening) | C | 2111.11
Firebox dimensions | — | 2111.7
Hearth and hearth extension reinforcing | D | 2111.1
Thickness of wall of firebox | E | 2111.6
Distance from top of opening to throat | F | 2111.8, 2111.8.1
Smoke chamber wall thickness dimensions | G | 2111.9
Chimney vertical reinforcing | H | 2111.4.1, 2113.3.1
Chimney horizontal reinforcing | J | 2111.4.2, 2113.3.2
Fireplace lintel | L | 2111.8
Chimney walls with flue lining | M | 2113.11
Effective flue area (based on area of fireplace opening and chimney) | P | 2113.16
Clearances From chimney From fireplace From combustible trim or materials Above roof | R | 2113.19 2111.12 2111.13 2113.9
Anchorage strap Number required Embedment into chimney Fasten to Number of bolts | S | 2111.5 2113.4
Footing Thickness Width | T | 2111.3

## 2113.9
TABLE 2113.9
"F" FACTOR FOR DETERMINING CHIMNEY DISTANCES
"F" FACTOR FOR DETERMINING CHIMNEY DISTANCES
TYPE OF FUEL | "F" FACTOR
| 600°F (316°C) and less | 600°F (316°C) to 1000°F (538°C) | Greater than 1000°F (538°C)
Gas | 2 | 2 | 3
No. 2 fuel oil | 2.5 | 2.5 | 3
No. 4, No. 6 fuel oils, solid fuels and incinerators | 3 | 3 | 3

## 2113.16(1)
TABLE 2113.16(1)
NET CROSS-SECTIONAL AREA OF ROUND FLUE SIZESa
FLUE SIZE, INSIDE DIAMETER (inches) | CROSS-SECTIONAL AREA (square inches)
6 | 28
7 | 38
8 | 50
10 | 78
10¾ | 90
12 | 113
15 | 176
18 | 254

## 2113.16(2)
TABLE 2113.16(2)
NET CROSS-SECTIONAL AREA OF SQUARE AND RECTANGULAR FLUE SIZESa
FLUE SIZE, OUTSIDE NOMINAL DIMENSIONS (inches) | CROSS-SECTIONAL AREA (square inches)
4.5 × 8.5 | 23
4.5 × 13 | 34
8 × 8 | 42
8.5 × 8.5 | 49
8 × 12 | 67
8.5 × 13 | 76
12 × 12 | 102
8.5 × 18 | 101
13 × 13 | 127
12 × 16 | 131
13 × 18 | 173
16 × 16 | 181
16 × 20 | 222
18 × 18 | 233
20 × 20 | 298
20 × 24 | 335
24 × 24 | 431

## 2304.6.1
TABLE 2304.6.1
MAXIMUM ALLOWABLE STRESS DESIGN WIND SPEED Vasd PERMITTED FOR WOOD STRUCTURAL PANEL WALL SHEATHING USED TO RESIST WIND PRESSURESa, b, c
MINIMUM NAIL |  | MINIMUM WOOD STRUCTURAL PANEL SPAN RATING | MINIMUM NOMINAL PANEL THICKNESS (inches) | MAXIMUM WALL STUD SPACING (inches) | PANEL NAIL SPACING |  | MAXIMUM ALLOWABLE STRESS DESIGN WIND SPEED, Vasdd (mph)
[5 empty] | Edges (inches o.c.) | Field (inches o.c.) | Wind exposure category
[7 empty] | B | C | D
6d common (2.0" × 0.113") | 1.5 | 24/0 | ³⁄₈ | 16 | 6 | 12 | 110 | 90 | 85
|  |  | ⁷⁄₁₆ |  | 6 | 12 | 110 | 100 | 90
|  | 24/16 |  | 16 | 6 | 6 | 150 | 125 | 110
8d common (2.5" × 0.131") |  |  |  |  | 6 | 12 | 130 | 110 | 105
[5 empty] | 6 | 6 | 150 | 125 | 110
|  |  |  | 24 | 6 | 12 | 110 | 90 | 85
[5 empty] | 6 | 6 | 110 | 90 | 85

## 2304.8(1)
TABLE 2304.8(1)
ALLOWABLE SPANS FOR LUMBER FLOOR AND ROOF SHEATHING
SPAN (inches) | MINIMUM NET THICKNESS (inches) OF LUMBER PLACED
| Perpendicular to supports |  | Diagonally to supports
| Surfaced drya | Surfaced unseasoned | Surfaced drya | Surfaced unseasoned
Floors
24 | ³⁄₄ | ²⁵⁄₃₂ | ³⁄₄ | ²⁵⁄₃₂
16 | ⁵⁄₈ | ¹¹⁄₁₆ | ⁵⁄₈ | ¹¹⁄₁₆
Roofs
24 | ⁵⁄₈ | ¹¹⁄₁₆ | ³⁄₄ | ²⁵⁄₃₂

## 2304.8(2)
TABLE 2304.8(2)
SHEATHING LUMBER, MINIMUM GRADE REQUIREMENTS: BOARD GRADE
SOLID FLOOR OR ROOF SHEATHING | SPACED ROOF SHEATHING | GRADING RULES
Utility | Standard | NLGA, WCLIB, WWPA
4 common or utility | 3 common or standard | NLGA, WCLIB, WWPA, NSLB or NELMA
No. 3 | No. 2 | SPIB
Merchantable | Construction common | RIS

## 2304.8(3)
TABLE 2304.8(3)
ALLOWABLE SPANS AND LOADS FOR WOOD STRUCTURAL PANEL SHEATHING AND SINGLE-FLOOR GRADES CONTINUOUS OVER TWO OR MORE SPANS WITH STRENGTH AXIS PERPENDICULAR TO SUPPORTSa
SHEATHING GRADES |  | ROOFb |  |  |  | FLOORc
Panel span rating roof/floor span | Panel thickness (inches) | Maximum span (inches) |  | Loadd (psf) |  | Maximum span (inches)
|  | With edge supporte | Without edge support | Total load | Live load
16/0 | ³⁄₈ | 16 | 16 | 40 | 30 | 0
20/0 | ³⁄₈ | 20 | 20 | 40 | 30 | 0
24/0 | ³⁄₈,⁷⁄₁₆,¹⁄₂ | 24 | 20g | 40 | 30 | 0
24/16 | ⁷⁄₁₆, ¹⁄₂ | 24 | 24 | 50 | 40 | 16
32/16 | ¹⁵⁄₃₂,¹⁄₂,⁵⁄₈ | 32 | 28 | 40 | 30 | 16g
40/20 | ¹⁹⁄₃₂,⁵⁄₈,³⁄₄,⁷⁄₈ | 40 | 32 | 40 | 30 | 20g, h
48/24 | ²³⁄₃₂,³⁄₄,⁷⁄₈ | 48 | 36 | 45 | 35 | 24
54/32 | ⁷⁄₈, 1 | 54 | 40 | 45 | 35 | 32
60/32 | ⁷⁄₈, 1¹⁄₈ | 60 | 48 | 45 | 35 | 32
SINGLE FLOOR GRADES |  | ROOFb |  |  |  | FLOORc
Panel span rating | Panel thickness (inches) | Maximum span (inches) |  | Loadd (psf) |  | Maximum span (inches)
|  | With edge supporte | Without edge support | Total load | Live load
16 o.c. | ¹⁄₂,¹⁹⁄₃₂,⁵⁄₈ | 24 | 24 | 50 | 40 | 16g
20 o.c. | ¹⁹⁄₃₂,⁵⁄₈,³⁄₄ | 32 | 32 | 40 | 30 | 20g, h
24 o.c. | ²³⁄₃₂,³⁄₄ | 48 | 36 | 35 | 25 | 24
32 o.c. | ⁷⁄₈, 1 | 48 | 40 | 50 | 40 | 32
48 o.c. | ¹³⁄₃₂, 1¹⁄₈ | 60 | 48 | 50 | 40 | 48

## 2304.8(4)
TABLE 2304.8(4)
ALLOWABLE SPAN FOR WOOD STRUCTURAL PANEL COMBINATION SUBFLOOR-UNDERLAYMENT (SINGLE FLOOR)a
(Panels Continuous Over Two or More Spans and Strength Axis Perpendicular to Supports)
IDENTIFICATION | MAXIMUM SPACING OF JOISTS (inches)
| 16 | 20 | 24 | 32 | 48
Species groupb | Thickness (inches)
1 | ¹⁄₂ | ⁵⁄₈ | ³⁄₄ | — | —
2, 3 | ⁵⁄₈ | ³⁄₄ | ⁷⁄₈ | — | —
4 | ³⁄₄ | ⁷⁄₈ | 1 | — | —
Single floor span ratingc | 16 o.c. | 20 o.c. | 24 o.c. | 32 o.c. | 48 o.c.

## 2304.8(5)
TABLE 2304.8(5)
ALLOWABLE LOAD (PSF) FOR WOOD STRUCTURAL PANEL ROOF SHEATHING CONTINUOUS OVER TWO OR MORE SPANS AND STRENGTH AXIS PARALLEL TO SUPPORTS
(Plywood Structural Panels Are Five-Ply, Five-Layer Unless Otherwise Noted)a
PANEL GRADE | THICKNESS (inch) | MAXIMUM SPAN (inches) | LOAD AT MAXIMUM SPAN (psf)
|  |  | Live | Total
Structural I sheathing | ⁷⁄₁₆ | 24 | 20 | 30
| ¹⁵⁄₃₂ | 24 | 35b | 45b
| ¹⁄₂ | 24 | 40b | 50b
| ¹⁹⁄₃₂, ⁵⁄₈ | 24 | 70 | 80
| ²³⁄₃₂, ³⁄₄ | 24 | 90 | 100
Sheathing, other grades covered in DOC PS 1 or DOC PS 2 | ⁷⁄₁₆ | 16 | 40 | 50
| ¹⁵⁄₃₂ | 24 | 20 | 25
| ¹⁄₂ | 24 | 25 | 30
| ¹⁹⁄₃₂ | 24 | 40b | 50b
| ⁵⁄₈ | 24 | 45b | 55b
| ²³⁄₃₂, ³⁄₄ | 24 | 60b | 65b

## 2304.9.3.2.1
TABLE 2304.9.3.2.1
FASTENING SCHEDULE FOR MECHANICALLY LAMINATED DECKING USING LAMINATIONS OF 2-INCH NOMINAL THICKNESS
MINIMUM NAIL SIZE (Length × Diameter) | MAXIMUM SPACING BETWEEN FACE NAILSa, b, c (inches) |  | NUMBER OF TOENAILS INTO SUPPORTSd
| Decking Supports ≤ 48 inches on center | Decking Supports > 48 inches on center
4" × 0.192" | 30 | 18 | 1
4" × 0.162" | 24 | 14 | 2
4" × 0.148" | 22 | 13 | 2
3½" × 0.162" | 20 | 12 | 2
3½" × 0.148" | 19 | 11 | 2
3½" × 0.135" | 17 | 10 | 2
3" × 0.148" | 11 | 7 | 2
3" × 0.128" | 9 | 5 | 2
2¾" × 0.148" | 10 | 6 | 2
2¾" × 0.131" | 9 | 6 | 3
2¾" × 0.120" | 8 | 5 | 3

## 2304.10.1
TABLE 2304.10.1 FASTENING SCHEDULE
DESCRIPTION OF BUILDING ELEMENTS | NUMBER AND TYPE OF FASTENER | SPACING AND LOCATION
Roof
1. Blocking between ceiling joists, rafters or trusses to top plate or other framing below | 3-8d common (2½" × 0.131"); or 3-10d box (3" × 0.128"); or 3-3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | Each end, toenail
Blocking between rafters or truss not at the wall top plate, to rafter or truss | 2-8d common (2½" × 0.131") 2-3" × 0.131" nails 2-3" 14 gage staples | Each end, toenail
| 2-16d common (3½" × 0.162") 3-3" × 0.131" nails 3-3" 14 gage staples | End nail
Flat blocking to truss and web filler | 16d common (3½" × 0.162") @ 6" o.c. 3" × 0.131" nails @ 6" o.c. 3" × 14 gage staples @ 6" o.c. | Face nail
2. Ceiling joists to top plate | 3-8d common (2½" × 0.131"); or 3-10d box (3" × 0.128"); or 3-3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | Each joist, toenail
2-16d common (3½" × 0.162")
3. Ceiling joist not attached to parallel rafter, laps over partitions (no thrust) (see Section 2308.7.3.1, Table 2308.7.3.1) | 3-16d common (3½" × 0.162"); or 4-10d box (3" × 0.128"); or 4-3" × 0.131" nails; or 4-3" 14 gage staples, ⁷⁄₁₆" crown | Face nail
4. Ceiling joist attached to parallel rafter (heel joint) (see Section 2308.7.3.1, Table 2308.7.3.1) | Per Table 2308.7.3.1 | Face nail
5. Collar tie to rafter | 3-10d common (3" × 0.148"); or 4-10d box (3" × 0.128"); or 4-3" × 0.131" nails; or 4-3" 14 gage staples, ⁷⁄₁₆" crown | Face nail
6. Rafter or roof truss to top plate (See Section 2308.7.5, Table 2308.7.5) | 3-10d common (3" × 0.148"); or 3-16d box (3½" × 0.135"); or 4-10d box (3" × 0.128"); or 4-3" × 0.131" nails; or 4-3" 14 gage staples, ⁷⁄₁₆" crown | Toenailc
7. Roof rafters to ridge valley or hip rafters; or roof rafter to 2-inch ridge beam | 2-16d common (3½" × 0.162"); or 3-10d box (3" × 0.128"); or 3-3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | End nail
| 3-10d common (3" × 0.148"); or 4-16d box (3½" × 0.135"); or 4-10d box (3" × 0.128"); or 4-3" × 0.131" nails; or 4-3" 14 gage staples, ⁷⁄₁₆" crown | Toenail
Wall
8. Stud to stud (not at braced wall panels) | 16d common (3½" × 0.162"); | 24" o.c. face nail
| 10d box (3" × 0.128"); or 3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | 16" o.c. face nail
9. Stud to stud and abutting studs at intersecting wall corners (at braced wall panels) | 16d common (3½" × 0.162"); or | 16" o.c. face nail
| 16d box (3½" × 0.135"); or | 12" o.c. face nail
| 3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | 12" o.c. face nail
10. Built-up header (2" to 2" header) | 16d common (3½" × 0.162"); or | 16" o.c. each edge, face nail
| 16d box (3½" × 0.135") | 12" o.c. each edge, face nail
11. Continuous header to stud | 4-8d common (2½" × 0.131"); or 4-10d box (3" × 0.128") | Toenail
12. Top plate to top plate | 16d common (3½" × 0.162"); or | 16" o.c. face nail
| 10d box (3" × 0.128"); or 3" × 0.131" nails; or 3" 14 gage staples, ⁷⁄₁₆" crown | 12" o.c. face nail
13. Top plate to top plate, at end joints | 8-16d common (3½" × 0.162"); or 12-10d box (3" × 0.128"); or 12-3" × 0.131" nails; or 12-3" 14 gage staples, ⁷⁄₁₆" crown | Each side of end joint, face nail (minimum 24" lap splice length each side of end joint)
14. Bottom plate to joist, rim joist, band joist or blocking (not at braced wall panels) | 16d common (3½" × 0.162"); or | 16" o.c. face nail
| 16d box (3½" × 0.135"); or 3" × 0.131" nails; or 3" 14 gage staples, ⁷⁄₁₆" crown | 12" o.c. face nail
15. Bottom plate to joist, rim joist, band joist or blocking at braced wall panels | 2-16d common (3½" × 0.162"); or 3-16d box (3½" × 0.135"); or 4-3" × 0.131" nails; or 4-3" 14 gage staples, ⁷⁄₁₆" crown | 16" o.c. face nail
16. Stud to top or bottom plate | 4-8d common (2½" × 0.131"); or 4-10d box (3" × 0.128"); or 4-3" × 0.131" nails; or 4-3" 14 gage staples, ⁷⁄₁₆" crown | Toenail
| 2-16d common (3½" × 0.162"); or 3-10d box (3" × 0.128"); or 3-3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | End nail
17. Top plates, laps at corners and intersections | 2-16d common (3½" × 0.162"); or 3-10d box (3" × 0.128"); or 3-3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | Face nail
18. 1" brace to each stud and plate | 2-8d common (2½" × 0.131"); or 2-10d box (3" × 0.128"); or 2-3" × 0.131" nails; or 2-3" 14 gage staples, ⁷⁄₁₆" crown | Face nail
19. 1" × 6" sheathing to each bearing | 2-8d common (2½" × 0.131"); or 2-10d box (3" × 0.128") | Face nail
20. 1" × 8" and wider sheathing to each bearing | 3-8d common (2½" × 0.131"); or 3-10d box (3" × 0.128") | Face nail
Floor
21. Joist to sill, top plate, or girder | 3-8d common (2½" × 0.131"); or 3-10d box (3" × 0.128"); or 3-3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | Toenail
22. Rim joist, band joist, or blocking to top plate, sill or other framing below | 8d common (2½" × 0.131"); or 10d box (3" × 0.128"); or 3" × 0.131" nails; or 3" 14 gage staples, ⁷⁄₁₆" crown | 6" o.c. face nail
23. 1" × 6" subfloor or less to each joist | 2-8d common (2½" × 0.131"); or 2-10d box (3" × 0.128") | Face nail
24. 2" subfloor to joist or girder | 2-16d common (3½" × 0.162") | Face nail
25. 2" planks (plank & beam – floor & roof) | 2-16d common (3½" × 0.162") | Each bearing, face nail
26. Built-up girders and beams, 2" lumber layers | 20d common (4" × 0.192") | 32" o.c., face nail at top and bottom staggered on opposite sides
| 10d box (3" × 0.128"); or 3" × 0.131" nails; or 3" 14 gage staples, ⁷⁄₁₆" crown | 24" o.c. face nail at top and bottom staggered on opposite sides
| And: 2-20d common (4" × 0.192"); or 3-10d box (3" × 0.128"); or 3-3" × 0.131" nails; or 3-3" 14 gage staples, ⁷⁄₁₆" crown | Ends and at each splice, face nail
27. Ledger strip supporting joists or rafters | 3-16d common (3½" × 0.162"); or 4-10d box (3" × 0.128"); or 4-3" × 0.131" nails; or 4-3" 14 gage staples, ⁷⁄₁₆" crown | Each joist or rafter, face nail
28. Joist to band joist or rim joist | 3-16d common (3½" × 0.162"); or 4-10d box (3" × 0.128"); or 4-3" × 0.131" nails; or 4-3" 14 gage staples, ⁷⁄₁₆" crown | End nail
29. Bridging or blocking to joist, rafter or truss | 2-8d common (2½" × 0.131"); or 2-10d box (3" × 0.128"); or 2-3" × 0.131" nails; or 2-3" 14 gage staples, ⁷⁄₁₆" crown | Each end, toenail
Wood structural panels (WSP), subfloor, roof and interior wall sheathing to framing and particleboard wall sheathing to framinga
|  | Edges (inches) | Intermediate supports (inches)
30. ¾" — ½" | 6d common or deformed (2" × 0.113") (subfloor and wall) | 6 | 12
| 8d common or deformed (2½" × 0.113") (roof) or RSRS-01 (2¾" × 0.113") nail (roof)d | 6 | 12
| 2¾" × 0.113" nail (subfloor and wall) | 6 | 12
| 1¾" 16 gage staple, ⁷⁄₁₆" crown (subfloor and wall) | 4 | 8
| 2¾" × 0.113" nail (roof) | 4 | 8
| 1¾" 16 gage staple, ⁷⁄₁₆" crown (roof) | 3 | 6
31. ¹⁹⁄₃₂" — ¾" | 8d common (2½" × 0.131"); or 6d deformed (2" × 0.113") (subfloor and wall) | 6 | 12
| 8d common or deformed (2½" × 0.131") or RSRS-01 (2¾" × 0.113") nail (roof)d | 6 | 12
| 2¾" × 0.113" nail; or 2" 16 gage staple, ⁷⁄₁₆" crown | 4 | 8
32. ⁷⁄₈" — 1¼" | 10d common (3" × 0.148"); or 8d deformed (2½" × 0.113") | 6 | 12
Other exterior wall sheathing
33. ½" fiberboardsheathingᵇ | 1½" galvanized roofing nail (⁷⁄₁₆" head diameter); or 1¼" 16 gage staple with ⁷⁄₁₆" or 1" crown | 3 | 6
34. ²⁵⁄₃₂" fiberboard sheathingᵇ | 1¾" galvanized roofing nail (⁷⁄₁₆" head diameter); or 1½" 16 gage staple with ⁷⁄₁₆" or 1" crown | 3 | 6
Wood structural panels, combination subfloor underlayment to framing
35. ¾" and less | 8d common (2½" × 0.131"); or 6d deformed (2" × 0.113") | 6 | 12
36. ⁷⁄₈" — 1" | 8d common (2½" × 0.131"); or 6d deformed (2½" × 0.131") | 6 | 12
37. 1⅛" — 1¼" | 10d common (3" × 0.148"); or 8d deformed (2½" × 0.131") | 6 | 12
Panel siding to framing
38. ½" or less | 6d corrosion-resistant (1⁷⁄₈" × 0.106"); or 6d corrosion-resistant casing (2" × 0.099") | 6 | 12
39. ⅝" | 8d corrosion-resistant (2¾" × 0.128"); or 8d corrosion-resistant casing (2½" × 0.113") | 6 | 12
Interior paneling
40. ¼" | 4d casing (1½" × 0.080"); or 4d finish (1½" × 0.072") | 6 | 12
41. ⅜" | 6d casing (2" × 0.099"); or 6d finish (Panel supports at 24 inches) | 6 | 12

## 2304.11
TABLE 2304.11
MINIMUM DIMENSIONS OF HEAVY TIMBER STRUCTURAL MEMBERS
|  | MINIMUM NOMINAL SOLID SAWN SIZE |  | MINIMUM GLUED LAMINATED NET SIZE |  | MINIMUM STRUCTURAL COMPOSITE LUMBER NET SIZE
|  | Width, Inch | Depth, Inch | Width, Inch | Depth, Inch | Width, Inch | Depth, Inch
Floor loads only or combined floor and roof loads | Columns; Framed sawn or glued-laminated timber arches that spring from the floor line; Framed timber trusses | 8 | 8 | 6³⁄₄ | 8¹⁄₄ | 7 | 7¹⁄₂
| Wood beams and girders | 6 | 10 | 5 | 10¹⁄₂ | 5¹⁄₄ | 9¹⁄₂
| Columns (roof and ceiling loads); Lower half of: wood-frame or glued-laminated arches that spring from the floor line or from grade | 6 | 8 | 5 | 8¹⁄₄ | 5¹⁄₄ | 7¹⁄₂
| Upper half of: wood-frame or glued-laminated arches that spring from the floor line or from grade | 6 | 6 | 5 | 6 | 5¹⁄₄ | 5¹⁄₂
| Framed timber trusses and other roof framing; Framed or glued-laminated arches that spring from the top of walls or wall abutments | 4ᵇ | 6 | 3ᵇ | 6⁷⁄₈‡ | 3¹⁄₂ᵇ | 5¹⁄₂

## 2305.2(1)
TABLE 2305.2(1)
eₙ VALUES (inches) FOR USE IN CALCULATING DIAPHRAGM AND SHEAR WALL DEFLECTION DUE TO FASTENER SLIP
(Structural I)ᵃ˙ᶜ
LOAD PER FASTENERᵇ (pounds) | FASTENER DESIGNATIONS
14-Ga staple x 2 inches long
60 | 0.011
80 | 0.018
100 | 0.028
120 | 0.04
140 | 0.053
160 | 0.068

## 2305.2(2)
TABLE 2305.2(2)
VALUES OF Gt FOR USE IN CALCULATING DEFLECTION OF WOOD STRUCTURAL PANEL SHEAR WALLS AND DIAPHRAGMS
VALUES OF Gt (lb/in. panel depth or width)
PANEL TYPE | SPAN RATING | Structural Sheathing |  |  |  | Structural I
|  | plywood |  |  |  | plywood
|  | 3-ply | 4-ply | 5-ply | OSB | 3-ply | 4-ply | 5-ply | OSB
Sheathing | 24/0 | 25000 | 32500 | 37500 | 77500 | 32500 | 42500 | 41500 | 77500
| 24/16 | 27000 | 35000 | 40500 | 83500 | 35000 | 45500 | 44500 | 83500
| 32/16 | 27000 | 35000 | 40500 | 83500 | 35000 | 45500 | 44500 | 83500
| 40/20 | 28500 | 37000 | 43000 | 88500 | 37000 | 48000 | 47500 | 88500
| 48/24 | 31000 | 40500 | 46500 | 96000 | 40500 | 52500 | 51000 | 96000
Single Floor | 16 o.c. | 27000 | 35000 | 40500 | 83500 | 35000 | 45500 | 44500 | 83500
| 20 o.c. | 28000 | 36500 | 42000 | 87000 | 36500 | 47500 | 46000 | 87000
| 24 o.c. | 30000 | 39000 | 45000 | 93000 | 39000 | 50500 | 49500 | 93000
| 32 o.c. | 36000 | 47000 | 54000 | 110000 | 47000 | 61000 | 59500 | 110000
| 48 o.c. | 50500 | 65500 | 76000 | 155000 | 65500 | 85000 | 83500 | 155000
PANEL TYPE |  | Structural Sheathing |  |  | Structural I
|  | A-A, A-C | Marine | All Other Grades | A-A, A-C | Marine | All Other Grades
Sanded Plywood | 2026-01-04 | 24000 | 31000 | 24000 | 31000 | 31000 | 31000
| 1¹⁄₃₂ | 25500 | 33000 | 25500 | 33000 | 33000 | 33000
| 2026-03-08 | 26000 | 34000 | 26000 | 34000 | 34000 | 34000
| ¹⁵⁄₃₂ | 38000 | 49500 | 38000 | 49500 | 49500 | 49500
| 2026-01-02 | 38500 | 50000 | 38500 | 50000 | 50000 | 50000
| ¹⁹⁄₃₂ | 49000 | 63500 | 49000 | 63500 | 63500 | 63500
| 2026-05-08 | 49500 | 64500 | 49500 | 64500 | 64500 | 64500
| ²³⁄₃₂ | 50500 | 65500 | 50500 | 65500 | 65500 | 65500
| 2026-03-04 | 51000 | 66500 | 51000 | 66500 | 66500 | 66500
| 2026-07-08 | 52500 | 68500 | 52500 | 68500 | 68500 | 68500
| 1 | 73500 | 95500 | 73500 | 95500 | 95500 | 95500
| 1¹⁄⁸ | 75000 | 97500 | 75000 | 97500 | 97500 | 97500

## 2306.1.4
TABLE 2306.1.4
ALLOWABLE LOADS FOR LUMBER DECKING
ALLOWABLE AREA LOADa, b
| Flexure | Deflection
Simple span | σᵇ = 8Fᵇ’d² / l²6 | σᴸ = 384ΔE’ d³ / 5l⁴ 12
Two-span continuous | σᵇ = 8Fᵇ’d² / l²6 | σᴸ = 185ΔE’ d³ / l⁴ 12
Combination simple- and two-span continuous | σᵇ = 8Fᵇ’d² / l²6 | σᴸ = 131ΔE’ d³ / l⁴ 12
Cantilevered pieces intermixed | σᵇ = 20Fᵇ’d² / 3l²6 | σᴸ = 105ΔE’ d³ / l⁴ 12
Controlled random layup
Mechanically laminated decking | σᵇ = 20Fᵇ’d² / 3l²6 | σᴸ = 100ΔE’ d³ / l⁴ 12
2-inch decking | σᵇ = 20Fᵇ’d² / 3l²6 | σᴸ = 100ΔE’ d³ / l⁴ 12
3-inch and 4-inch decking | σᵇ = 20Fᵇ’d² / 3l²6 | σᴸ = 116ΔE’ d³ / l⁴ 12

## 2306.2(1)
TABLE 2306.2(1)
ALLOWABLE SHEAR VALUES (POUNDS PER FOOT) FOR WOOD STRUCTURAL PANEL DIAPHRAGMS UTILIZING STAPLES WITH FRAMING OF DOUGLAS FIR-LARCH, OR SOUTHERN PINEa FOR WIND OR SEISMIC LOADINGf
[5 empty] | BLOCKED DIAPHRAGMS |  |  |  | UNBLOCKED DIAPHRAGMS
[5 empty] | Fastener spacing (inches) at diaphragm boundaries (all cases) at continuous panel edges parallel to load (Cases 3, 4), and at all panel edges (Cases 5, 6)b |  |  |  | Case 1 (No unblocked edges or continuous joints parallel to load) | All other configurations (Cases 2, 3, 4, 5 and 6)
[5 empty] | 6 | 4 | 2¹⁄₂c | 2c
Fastener spacing (inches) at other panel edges (Cases 1, 2, 3 and 4)b
[5 empty] | 6 | 6 | 4 | 3
Structural I grades | 1¹⁄₂ 16 gage | 1 | ³⁄₈ | 2 | 175 | 235 | 350 | 400 | 155 | 115
|  |  |  | 3 | 200 | 265 | 395 | 450
|  |  | ¹⁵⁄₃₂ | 2 | 175 | 235 | 350 | 400
|  |  |  | 3 | 200 | 265 | 395 | 450
Sheathing, single floor and other grades covered in DOC PS 1 and PS 2 | 1¹⁄₂ 16 gage | 1 | ³⁄₈ | 2 | 160 | 210 | 315 | 360 | 140 | 105
|  |  |  | 3 | 180 | 235 | 355 | 400
|  |  | ⁷⁄₁₆ | 2 | 165 | 225 | 335 | 380
|  |  |  | 3 | 190 | 250 | 375 | 425
|  |  | ¹⁵⁄₃₂ | 2 | 160 | 210 | 315 | 360
|  |  |  | 3 | 180 | 235 | 355 | 405
|  |  | ¹⁹⁄₃₂ | 2 | 175 | 235 | 350 | 400
|  |  |  | 3 | 200 | 265 | 395 | 450

## 2306.2(2)
TABLE 2306.2(2)
ALLOWABLE SHEAR VALUES (POUNDS PER FOOT) FOR WOOD STRUCTURAL PANEL BLOCKED DIAPHRAGMS UTILIZING MULTIPLE ROWS OF STAPLES (HIGH-LOAD DIAPHRAGMS) WITH FRAMING OF DOUGLAS FIR-LARCH OR SOUTHERN PINEa FOR WIND OR SEISMIC LOADINGb, g, h
BLOCKED DIAPHRAGMS
Cases 1 and 2d
Fastener Spacing Per Line at Boundaries (inches)
[6 empty] | 4 |  | 2¹⁄₂ |  | 2
Fastener Spacing Per Line at Other Panel Edges (inches)
[6 empty] | 6 | 4 | 4 | 3 | 3 | 2
Structural I grades | 14 gage staples | 2 | ¹⁵⁄₃₂ | 3 | 2 | 600 | 600 | 860 | 960 | 1060 | 1200
|  |  |  | 4 | 3 | 860 | 900 | 1160 | 1295 | 1295 | 1400
|  |  | ¹⁹⁄₃₂ | 3 | 2 | 600 | 600 | 875 | 960 | 1075 | 1200
|  |  |  | 4 | 3 | 875 | 900 | 1175 | 1440 | 1475 | 1795
Sheathing single floor and other grades covered in DOC PS 1 and PS 2 | 14 gage staples | 2 | ¹⁵⁄₃₂ | 3 | 2 | 540 | 540 | 735 | 865 | 915 | 1080
|  |  |  | 4 | 3 | 735 | 810 | 1005 | 1105 | 1105 | 1195
|  |  | ¹⁹⁄₃₂ | 3 | 2 | 600 | 600 | 865 | 960 | 1065 | 1200
|  |  |  | 4 | 3 | 865 | 900 | 1130 | 1430 | 1370 | 1485
|  |  | ²³⁄₃₂ | 4 | 3 | 865 | 900 | 1130 | 1490 | 1430 | 1545

## 2306.3(1)
TABLE 2306.3(1)
ALLOWABLE SHEAR VALUES (POUNDS PER FOOT) FOR WOOD STRUCTURAL PANEL SHEAR WALLS UTILIZING STAPLES WITH FRAMING OF DOUGLAS FIR-LARCH OR SOUTHERN PINEa FOR WIND OR SEISMIC LOADINGb, f, g, i
|  |  | PANELS APPLIED DIRECT TO FRAMING |  |  |  |  | PANELS APPLIED OVER ¹⁄₂" OR ⁵⁄₈" GYPSUM SHEATHING
|  |  | Staple length and gage (inches)h | Fastener spacing at panel edges (inches) |  |  |  | Staple length and gage (inches)h | Fastener spacing at panel edges (inches)
|  |  |  | 6 | 4 | 3 | 2d |  | 6 | 4 | 3 | 2d
Structural I sheathing | ³⁄₈ | 1 | 1¹⁄₂ 16 Gage | 155 | 235 | 315 | 400 | 2 16 Gage | 155 | 235 | 310 | 400
| ⁷⁄₁₆ |  |  | 170 | 260 | 345 | 440 |  | 155 | 235 | 310 | 400
| ¹⁵⁄₃₂ |  |  | 185 | 280 | 375 | 475 |  | 155 | 235 | 300 | 400
Sheathing, plywood sidinge except Group 5 Species | ⁵⁄₁₆c or ¹⁄₄c | 1 | 1¹⁄₂ 16 Gage | 145 | 220 | 295 | 375 | 2 16 Gage | 110 | 165 | 220 | 285
| ³⁄₈ |  |  | 140 | 210 | 280 | 360 |  | 140 | 210 | 280 | 360
| ⁷⁄₁₆ |  |  | 155 | 230 | 310 | 395 |  | 140 | 210 | 280 | 360
| ¹⁵⁄₃₂ |  |  | 170 | 255 | 335 | 430 |  | 140 | 210 | 280 | 360
| ¹⁹⁄₃₂ |  | 1³⁄₄ 16 Gage | 185 | 280 | 375 | 475 |  | — | — | — | —

## 2306.3(2)
TABLE 2306.3(2)
ALLOWABLE SHEAR VALUES (plf) FOR WIND OR SEISMIC LOADING ON SHEAR WALLS OF FIBERBOARD SHEATHING BOARD CONSTRUCTION UTILIZING STAPLES FOR TYPE V CONSTRUCTION ONLYa, b, c, d, e
ALLOWABLE SHEAR VALUE (pounds per linear foot) STAPLE SPACING AT PANEL EDGES (inches)a
|  | 4 | 3 | 2
¹⁄₂" or ²⁵⁄₃₂" Structural | No. 16 gage galvanized staple, ⁷⁄₁₆ inch crown 1³⁄₄ inches long | 150 | 200 | 225
| No. 16 gage galvanized staple, 1 inch crown 1³⁄₄ inches long | 220 | 290 | 325

## 2306.3(3)
TABLE 2306.3(3)
ALLOWABLE SHEAR VALUES FOR WIND OR SEISMIC FORCES FOR SHEAR WALLS OF LATH AND PLASTER OR GYPSUM BOARD WOOD FRAMED WALL ASSEMBLIES UTILIZING STAPLES
TYPE OF MATERIAL | THICKNESS OF MATERIAL | WALL CONSTRUCTION | STAPLE SPACINGb MAXIMUM (inches) | SHEAR VALUEa, c (plf) | MINIMUM STAPLE SIZE f, g
1. Expanded metal or woven wire lath and portland cement plaster | ⁷⁄₈" | Unblocked | 6 | 180 | No. 16 gage galv. staple, ⁷⁄₈" legs
2. Gypsum lath, plain or perforated | ³⁄₈" lath and ¹⁄₂" plaster | Unblocked | 5 | 100 | No. 16 gage galv. staple, 1¹⁄₈" long
3. Gypsum sheathing | ¹⁄₂" × 2' × 8' | Unblocked | 4 | 75
| ¹⁄₂" ×4' | Blockedd | 4 | 175 | No. 16 gage galv. staple, 1³⁄₄" long
|  | Unblocked | 7 | 100
4. Gypsum board, gypsum veneer base or water-resistant gypsum backing board | ¹⁄₂" | Unblockedd | 7 | 75
|  | Unblockedd | 4 | 110
|  | Unblocked | 7 | 100
|  | Unblocked | 4 | 125 | No. 16 gage galv. staple, 1¹⁄₂" long
|  | Blockede | 7 | 125
|  | Blockede | 4 | 150
| ⁵⁄₈" | Unblockedd | 7 | 115
|  | Unblockedd | 4 | 145
|  | Blockede | 7 | 145 | No. 16 gage galv. staple, 1⁵⁄₈" long
|  | Blockede | 4 | 175
|  | Blockede Two-ply | Base ply: 9 Face ply: 7 | 250 | No. 16 gage galv. staple 1⁵⁄₈" long No. 15 gage galv. staple, 2¹⁄₄" long

## 2308.2.1
TABLE 2308.2.1
ALLOWABLE STORY HEIGHT
SEISMIC DESIGN CATEGORY | ALLOWABLE STORY ABOVE GRADE PLANE
A and B | Three stories
C | Two stories
Da | One story

## 2308.4.1.1(1)
TABLE 2308.4.1.1(1)
HEADER AND GIRDER SPANSa, b, c, d FOR EXTERIOR BEARING WALLS
(Maximum spans for Douglas Fir-Larch, Hem-Fir, Southern Pine and Spruce-Pine-Fir and required number of jack studs)
Building widthe (feet)
HEADERS AND GIRDERS SUPPORTING | SIZE | 12 |  | 24 |  | 36
|  | Spang | NJf | Spang | NJf | Spang | NJf
Roof and ceiling | 2-2 × 4 | 4-1 | 1 | 3-1 | 1 | 2-7 | 1
| 2-2 × 6 | 6-1 | 1 | 4-7 | 1 | 3-10 | 1
| 2-2 × 8 | 7-7 | 1 | 5-9 | 1 | 4-10 | 2
| 2-2 × 10 | 9-1 | 1 | 6-10 | 2 | 5-9 | 2
| 2-2 × 12 | 10-7 | 2 | 8-1 | 2 | 6-10 | 2
| 3-2 × 8 | 9-5 | 1 | 7-3 | 1 | 6-1 | 1
| 3-2 × 10 | 11-3 | 1 | 8-7 | 1 | 7-3 | 2
| 3-2 × 12 | 13-2 | 1 | 10-1 | 2 | 8-6 | 2
| 4-2 × 8 | 10-11 | 1 | 8-4 | 1 | 7-1 | 1
| 4-2 × 10 | 12-11 | 1 | 9-11 | 1 | 8-4 | 1
| 4-2 × 12 | 15-3 | 1 | 11-8 | 2 | 9-10 | 2
Roof, ceiling and one center-bearing floor | 2-2 × 4 | 3-3 | 1 | 2-6 | 1 | 2-2 | 1
| 2-2 × 6 | 4-10 | 1 | 3-9 | 1 | 3-3 | 2
| 2-2 × 8 | 6-1 | 1 | 4-10 | 2 | 4-1 | 2
| 2-2 × 10 | 7-3 | 2 | 5-8 | 2 | 4-10 | 2
| 2-2 × 12 | 8-6 | 2 | 6-8 | 2 | 5-8 | 2
| 3-2 × 8 | 7-8 | 1 | 6-1 | 1 | 5-1 | 2
| 3-2 × 10 | 9-1 | 1 | 7-2 | 2 | 6-1 | 2
| 3-2 × 12 | 10-8 | 2 | 8-5 | 2 | 7-2 | 2
| 4-2 × 8 | 8-10 | 1 | 6-11 | 1 | 5-11 | 1
| 4-2 × 10 | 10-6 | 1 | 8-3 | 2 | 7-1 | 2
| 4-2 × 12 | 12-4 | 1 | 9-8 | 2 | 8-3 | 2
Roof, ceiling and one clear span floor | 2-2 × 4 | 2-11 | 1 | 2-3 | 1 | 1-10 | 1
| 2-2 × 6 | 4-4 | 1 | 3-4 | 2 | 2-10 | 2
| 2-2 × 8 | 5-6 | 2 | 4-3 | 2 | 3-7 | 2
| 2-2 × 10 | 6-7 | 2 | 5-1 | 2 | 4-2 | 2
| 2-2 × 12 | 7-9 | 2 | 5-11 | 2 | 4-11 | 3
| 3-2 × 8 | 6-11 | 1 | 5-3 | 2 | 4-5 | 2
| 3-2 × 10 | 8-3 | 2 | 6-3 | 2 | 5-3 | 2
| 3-2 × 12 | 9-8 | 2 | 7-5 | 2 | 6-2 | 2
| 4-2 × 8 | 8-1 | 1 | 6-1 | 1 | 5-1 | 2
| 4-2 × 10 | 9-6 | 1 | 7-3 | 2 | 6-1 | 2
| 4-2 × 12 | 11-2 | 2 | 8-6 | 2 | 7-2 | 2
Roof, ceiling and two center-bearing floors | 2-2 × 4 | 2-8 | 1 | 2-1 | 1 | 1-9 | 1
| 2-2 × 6 | 4-1 | 1 | 3-2 | 2 | 2-8 | 2
| 2-2 × 8 | 5-1 | 2 | 4-1 | 2 | 3-5 | 2
| 2-2 × 10 | 6-1 | 2 | 4-9 | 2 | 4-1 | 2
| 2-2 × 12 | 7-1 | 2 | 5-7 | 2 | 4-9 | 3
| 3-2 × 8 | 6-4 | 1 | 5-1 | 2 | 4-3 | 2
| 3-2 × 10 | 7-6 | 2 | 5-11 | 2 | 5-1 | 2
| 3-2 × 12 | 8-10 | 2 | 7-1 | 2 | 5-11 | 2
| 4-2 × 8 | 7-3 | 1 | 5-9 | 1 | 4-11 | 2
| 4-2 × 10 | 8-8 | 1 | 6-10 | 2 | 5-10 | 2
| 4-2 × 12 | 10-2 | 2 | 8-1 | 2 | 6-10 | 2
Roof, ceiling and two clear span floors | 2-2 × 4 | 2-3 | 1 | 1-8 | 1 | 1-4 | 1
| 2-2 × 6 | 3-4 | 1 | 2-6 | 2 | 2-2 | 2
| 2-2 × 8 | 4-3 | 2 | 3-3 | 2 | 2-8 | 2
| 2-2 × 10 | 5-1 | 2 | 3-10 | 2 | 3-2 | 3
| 2-2 × 12 | 5-11 | 2 | 4-6 | 3 | 3-9 | 3
| 3-2 × 8 | 5-3 | 1 | 4-1 | 2 | 3-5 | 2
| 3-2 × 10 | 6-3 | 2 | 4-9 | 2 | 4-1 | 2
| 3-2 × 12 | 7-5 | 2 | 5-8 | 2 | 4-9 | 3
| 4-2 × 8 | 6-1 | 1 | 4-8 | 2 | 3-11 | 2
| 4-2 × 10 | 7-3 | 2 | 5-6 | 2 | 4-8 | 2
| 4-2 × 12 | 8-6 | 2 | 6-6 | 2 | 5-6 | 2

## 2308.4.1.1(2)
TABLE 2308.4.1.1(2)
HEADER AND GIRDER SPANSa, b FOR INTERIOR BEARING WALLS
(Maximum spans for Douglas Fir-Larch, Hem-Fir, Southern Pine and Spruce-Pine-Fir and required number of jack studs)
Building widthc (feet)
| SIZE | 12 |  | 24 |  | 36
|  | Spane | NJd | Spane | NJd | Spane | NJd
One Floor Only | 2-2 × 4 | 4-1 | 1 | 2-10 | 1 | 2-4 | 1
| 2-2 × 6 | 6-1 | 1 | 4-4 | 1 | 3-6 | 1
| 2-2 × 8 | 7-9 | 1 | 5-5 | 1 | 4-5 | 2
| 2-2 × 10 | 9-2 | 1 | 6-6 | 2 | 5-3 | 2
| 2-2 × 12 | 10-9 | 1 | 7-7 | 2 | 6-3 | 2
| 3-2 × 8 | 9-8 | 1 | 6-10 | 1 | 5-7 | 1
| 3-2 × 10 | 11-5 | 1 | 8-1 | 1 | 6-7 | 2
| 3-2 × 12 | 13-6 | 1 | 9-6 | 2 | 7-9 | 2
| 4-2 × 8 | 11-2 | 1 | 7-11 | 1 | 6-5 | 1
| 4-2 × 10 | 13-3 | 1 | 9-4 | 1 | 7-8 | 1
| 4-2 × 12 | 15-7 | 1 | 11-1 | 1 | 9-1 | 2
Two Floors | 2-2 × 4 | 2-7 | 1 | 1-11 | 1 | 1-7 | 1
| 2-2 × 6 | 3-11 | 1 | 2-11 | 2 | 2-5 | 2
| 2-2 × 8 | 5-1 | 1 | 3-8 | 2 | 3-1 | 2
| 2-2 × 10 | 5-11 | 2 | 4-4 | 2 | 3-7 | 2
| 2-2 × 12 | 6-11 | 2 | 5-2 | 2 | 4-3 | 3
| 3-2 × 8 | 6-3 | 1 | 4-7 | 2 | 3-10 | 2
| 3-2 × 10 | 7-5 | 1 | 5-6 | 2 | 4-6 | 2
| 3-2 × 12 | 8-8 | 2 | 6-5 | 2 | 5-4 | 2
| 4-2 × 8 | 7-2 | 1 | 5-4 | 1 | 4-5 | 2
| 4-2 × 10 | 8-6 | 1 | 6-4 | 2 | 5-3 | 2
| 4-2 × 12 | 10-1 | 1 | 7-5 | 2 | 6-2 | 2

## 2308.4.2.1(1)
TABLE 2308.4.2.1(1)
FLOOR JOIST SPANS FOR COMMON LUMBER SPECIES
(Residential sleeping areas, live load = 30 psf, L/Δ = 360)
|  |  | DEAD LOAD = 10 psf |  |  |  | DEAD LOAD = 20 psf
|  |  | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12
Maximum floor joist spans
|  |  | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.)
12 | Douglas Fir-Larch | SS | 12-6 | 16-6 | 21-0 | 25-7 | 12-6 | 16-6 | 21-0 | 25-7
| Douglas Fir-Larch | #1 | 12-1 | 15-10 | 20-3 | 24-8 | 12-1 | 15-7 | 19-0 | 22-0
| Douglas Fir-Larch | #2 | 11-10 | 15-7 | 19-10 | 23-0 | 11-6 | 14-7 | 17-9 | 20-7
| Douglas Fir-Larch | #3 | 9-8 | 12-4 | 15-0 | 17-5 | 8-8 | 11-1 | 13-5 | 15-7
| Hem-Fir | SS | 11-10 | 15-7 | 19-10 | 24-2 | 11-10 | 15-7 | 19-10 | 24-2
| Hem-Fir | #1 | 11-7 | 15-3 | 19-5 | 23-7 | 11-7 | 15-2 | 18-6 | 21-6
| Hem-Fir | #2 | 11-1 | 14-6 | 18-6 | 22-6 | 11-1 | 14-4 | 17-6 | 20-4
| Hem-Fir | #3 | 9-8 | 12-4 | 15-0 | 17-5 | 8-8 | 11-1 | 13-5 | 15-7
| Southern Pine | SS | 12-3 | 16-2 | 20-8 | 25-1 | 12-3 | 16-2 | 20-8 | 25-1
| Southern Pine | #1 | 11-10 | 15-7 | 19-10 | 24-2 | 11-10 | 15-7 | 18-7 | 22-0
| Southern Pine | #2 | 11-3 | 14-11 | 18-1 | 21-4 | 10-9 | 13-8 | 16-2 | 19-1
| Southern Pine | #3 | 9-2 | 11-6 | 14-0 | 16-6 | 8-2 | 10-3 | 12-6 | 14-9
| Spruce-Pine-Fir | SS | 11-7 | 15-3 | 19-5 | 23-7 | 11-7 | 15-3 | 19-5 | 23-7
| Spruce-Pine-Fir | #1 | 11-3 | 14-11 | 19-0 | 23-0 | 11-3 | 14-7 | 17-9 | 20-7
| Spruce-Pine-Fir | #2 | 11-3 | 14-11 | 19-0 | 23-0 | 11-3 | 14-7 | 17-9 | 20-7
| Spruce-Pine-Fir | #3 | 9-8 | 12-4 | 15-0 | 17-5 | 8-8 | 11-1 | 13-5 | 15-7
16 | Douglas Fir-Larch | SS | 11-4 | 15-0 | 19-1 | 23-3 | 11-4 | 15-0 | 19-1 | 23-0
| Douglas Fir-Larch | #1 | 10-11 | 14-5 | 18-5 | 21-4 | 10-8 | 13-6 | 16-5 | 19-1
| Douglas Fir-Larch | #2 | 10-9 | 14-1 | 17-2 | 19-11 | 9-11 | 12-7 | 15-5 | 17-10
| Douglas Fir-Larch | #3 | 8-5 | 10-8 | 13-0 | 15-1 | 7-6 | 9-6 | 11-8 | 13-6
| Hem-Fir | SS | 10-9 | 14-2 | 18-0 | 21-11 | 10-9 | 14-2 | 18-0 | 21-11
| Hem-Fir | #1 | 10-6 | 13-10 | 17-8 | 20-9 | 10-4 | 13-1 | 16-0 | 18-7
| Hem-Fir | #2 | 10-1 | 13-2 | 16-10 | 19-8 | 9-10 | 12-5 | 15-2 | 17-7
| Hem-Fir | #3 | 8-5 | 10-8 | 13-0 | 15-1 | 7-6 | 9-6 | 11-8 | 13-6
| Southern Pine | SS | 11-2 | 14-8 | 18-9 | 22-10 | 11-2 | 14-8 | 18-9 | 22-10
| Southern Pine | #1 | 10-9 | 14-2 | 18-0 | 21-4 | 10-9 | 13-9 | 16-1 | 19-1
| Southern Pine | #2 | 10-3 | 13-3 | 15-8 | 18-6 | 9-4 | 11-10 | 14-0 | 16-6
| Southern Pine | #3 | 7-11 | 10-10 | 12-1 | 14-4 | 7-1 | 8-11 | 10-10 | 12-10
| Spruce-Pine-Fir | SS | 10-6 | 13-10 | 17-8 | 21-6 | 10-6 | 13-10 | 17-8 | 21-4
| Spruce-Pine-Fir | #1 | 10-3 | 13-6 | 17-2 | 19-11 | 9-11 | 12-7 | 15-5 | 17-10
| Spruce-Pine-Fir | #2 | 10-3 | 13-6 | 17-2 | 19-11 | 9-11 | 12-7 | 15-5 | 17-10
| Spruce-Pine-Fir | #3 | 8-5 | 10-8 | 13-0 | 15-1 | 7-6 | 9-6 | 11-8 | 13-6
19.2 | Douglas Fir-Larch | SS | 10-8 | 14-1 | 18-0 | 21-10 | 10-8 | 14-1 | 18-0 | 21-0
| Douglas Fir-Larch | #1 | 10-4 | 13-7 | 16-9 | 19-6 | 9-8 | 12-4 | 15-0 | 17-5
| Douglas Fir-Larch | #2 | 10-1 | 12-10 | 15-8 | 18-3 | 9-1 | 11-6 | 14-1 | 16-3
| Douglas Fir-Larch | #3 | 7-8 | 9-9 | 11-10 | 13-9 | 6-10 | 8-8 | 10-7 | 12-4
| Hem-Fir | SS | 10-1 | 13-4 | 17-0 | 20-8 | 10-1 | 13-4 | 17-0 | 20-7
| Hem-Fir | #1 | 9-10 | 13-0 | 16-4 | 19-0 | 9-6 | 12-1 | 14-8 | 17-0
| Hem-Fir | #2 | 9-5 | 12-5 | 15-6 | 17-1 | 8-11 | 11-4 | 13-10 | 16-1
| Hem-Fir | #3 | 7-8 | 9-9 | 11-10 | 13-9 | 6-10 | 8-8 | 10-7 | 12-4
| Southern Pine | SS | 10-6 | 13-10 | 17-8 | 21-6 | 10-6 | 13-10 | 17-8 | 21-6
| Southern Pine | #1 | 10-1 | 13-4 | 16-5 | 19-6 | 9-11 | 12-7 | 14-8 | 17-5
| Southern Pine | #2 | 9-6 | 12-1 | 14-4 | 16-10 | 8-6 | 10-10 | 12-10 | 15-1
| Southern Pine | #3 | 7-3 | 9-1 | 11-1 | 13-1 | 6-5 | 8-2 | 9-10 | 11-8
| Spruce-Pine-Fir | SS | 9-10 | 13-0 | 16-7 | 20-2 | 9-10 | 13-0 | 16-7 | 19-6
| Spruce-Pine-Fir | #1 | 9-8 | 12-9 | 15-8 | 18-3 | 9-1 | 11-6 | 14-1 | 16-3
| Spruce-Pine-Fir | #2 | 9-8 | 12-9 | 15-8 | 18-3 | 9-1 | 11-6 | 14-1 | 16-3
| Spruce-Pine-Fir | #3 | 7-8 | 9-9 | 11-10 | 13-9 | 6-10 | 8-8 | 10-7 | 12-4
24 | Douglas Fir-Larch | SS | 9-11 | 13-1 | 16-8 | 20-3 | 9-11 | 13-1 | 16-2 | 18-9
| Douglas Fir-Larch | #1 | 9-7 | 12-4 | 15-0 | 17-5 | 8-8 | 11-1 | 13-5 | 15-7
| Douglas Fir-Larch | #2 | 9-1 | 11-6 | 14-1 | 16-3 | 8-1 | 10-3 | 12-7 | 14-7
| Douglas Fir-Larch | #3 | 6-10 | 8-8 | 10-7 | 12-4 | 6-2 | 7-9 | 9-6 | 11-1
| Hem-Fir | SS | 9-4 | 12-4 | 15-9 | 19-2 | 9-4 | 12-4 | 15-9 | 18-5
| Hem-Fir | #1 | 9-2 | 12-1 | 14-8 | 17-0 | 8-6 | 10-9 | 13-1 | 15-2
| Hem-Fir | #2 | 8-9 | 11-4 | 13-10 | 16-1 | 8-1 | 10-2 | 12-5 | 14-4
| Hem-Fir | #3 | 6-10 | 8-8 | 10-7 | 12-4 | 6-2 | 7-9 | 9-6 | 11-1
| Southern Pine | SS | 9-9 | 12-10 | 16-5 | 19-11 | 9-9 | 12-10 | 16-5 | 19-8
| Southern Pine | #1 | 9-4 | 12-4 | 14-8 | 17-5 | 8-10 | 11-3 | 13-1 | 15-7
| Southern Pine | #2 | 8-6 | 10-10 | 12-10 | 15-1 | 7-7 | 9-8 | 11-5 | 13-6
| Southern Pine | #3 | 6-5 | 8-2 | 9-10 | 11-8 | 5-9 | 7-3 | 8-10 | 10-5
| Spruce-Pine-Fir | SS | 9-2 | 12-1 | 15-5 | 18-9 | 9-2 | 12-1 | 15-0 | 17-5
| Spruce-Pine-Fir | #1 | 8-11 | 11-6 | 14-1 | 16-3 | 8-1 | 10-3 | 12-7 | 14-7
| Spruce-Pine-Fir | #2 | 8-11 | 11-6 | 14-1 | 16-3 | 8-1 | 10-3 | 12-7 | 14-7
| Spruce-Pine-Fir | #3 | 6-10 | 8-8 | 10-7 | 12-4 | 6-2 | 7-9 | 9-6 | 11-1

## 2308.4.2.1(2)
TABLE 2308.4.2.1(2)
FLOOR JOIST SPANS FOR COMMON LUMBER SPECIES
(Residential living areas, live load = 40 psf, L/Δ = 360)
|  |  | DEAD LOAD = 10 psf |  |  |  | DEAD LOAD = 20 psf
|  |  | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12
Maximum floor joist spans
|  |  | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.) | (ft.-in.)
12 | Douglas Fir-Larch | SS | 11-4 | 15-0 | 19-1 | 23-3 | 11-4 | 15-0 | 19-1 | 23-3
| Douglas Fir-Larch | #1 | 10-11 | 14-5 | 18-5 | 22-0 | 10-11 | 14-2 | 17-4 | 20-1
| Douglas Fir-Larch | #2 | 10-9 | 14-2 | 17-9 | 20-7 | 10-6 | 13-3 | 16-3 | 18-10
| Douglas Fir-Larch | #3 | 8-8 | 11-1 | 13-5 | 15-7 | 7-11 | 10-1 | 12-3 | 14-3
| Hem-Fir | SS | 10-9 | 14-2 | 18-0 | 21-11 | 10-9 | 14-2 | 18-0 | 21-11
| Hem-Fir | #1 | 10-6 | 13-10 | 17-8 | 21-6 | 10-6 | 13-10 | 16-11 | 19-7
| Hem-Fir | #2 | 10-1 | 13-2 | 16-10 | 20-4 | 10-1 | 13-1 | 16-0 | 18-6
| Hem-Fir | #3 | 8-8 | 11-1 | 13-5 | 15-7 | 7-11 | 10-1 | 12-3 | 14-3
| Southern Pine | SS | 11-2 | 14-8 | 18-9 | 22-10 | 11-2 | 14-8 | 18-9 | 22-10
| Southern Pine | #1 | 10-9 | 14-2 | 18-0 | 21-11 | 10-9 | 14-2 | 16-11 | 20-1
| Southern Pine | #2 | 10-3 | 13-6 | 16-2 | 19-1 | 9-10 | 12-6 | 14-9 | 17-5
| Southern Pine | #3 | 8-2 | 10-3 | 12-6 | 14-9 | 7-5 | 9-5 | 11-5 | 13-6
| Spruce-Pine-Fir | SS | 10-6 | 13-10 | 17-8 | 21-6 | 10-6 | 13-10 | 17-8 | 21-6
| Spruce-Pine-Fir | #1 | 10-3 | 13-6 | 17-3 | 20-7 | 10-3 | 13-3 | 16-3 | 18-10
| Spruce-Pine-Fir | #2 | 10-3 | 13-6 | 17-3 | 20-7 | 10-3 | 13-3 | 16-3 | 18-10
| Spruce-Pine-Fir | #3 | 8-8 | 11-1 | 13-5 | 15-7 | 7-11 | 10-1 | 12-3 | 14-3
16 | Douglas Fir-Larch | SS | 10-4 | 13-7 | 17-4 | 21-1 | 10-4 | 13-7 | 17-4 | 21-0
| Douglas Fir-Larch | #1 | 9-11 | 13-1 | 16-5 | 19-1 | 9-8 | 12-4 | 15-0 | 17-5
| Douglas Fir-Larch | #2 | 9-9 | 12-7 | 15-5 | 17-10 | 9-1 | 11-6 | 14-1 | 16-3
| Douglas Fir-Larch | #3 | 7-6 | 9-6 | 11-8 | 13-6 | 6-10 | 8-8 | 10-7 | 12-4
| Hem-Fir | SS | 9-9 | 12-10 | 16-5 | 19-11 | 9-9 | 12-10 | 16-5 | 19-11
| Hem-Fir | #1 | 9-6 | 12-7 | 16-0 | 18-7 | 9-6 | 12-1 | 14-8 | 17-0
| Hem-Fir | #2 | 9-1 | 12-1 | 15-2 | 17-7 | 8-11 | 11-4 | 13-10 | 16-1
| Hem-Fir | #3 | 7-6 | 9-6 | 11-8 | 13-6 | 6-10 | 8-8 | 10-7 | 12-4
| Southern Pine | SS | 10-2 | 13-4 | 17-0 | 20-9 | 10-2 | 13-4 | 17-0 | 20-9
| Southern Pine | #1 | 9-9 | 12-10 | 16-1 | 19-1 | 9-9 | 12-7 | 14-8 | 17-5
| Southern Pine | #2 | 9-4 | 11-10 | 14-0 | 16-6 | 8-6 | 10-10 | 12-10 | 15-1
| Southern Pine | #3 | 7-1 | 8-11 | 10-10 | 12-10 | 6-5 | 8-2 | 9-10 | 11-8
| Spruce-Pine-Fir | SS | 9-6 | 12-7 | 16-0 | 19-6 | 9-6 | 12-7 | 16-0 | 19-6
| Spruce-Pine-Fir | #1 | 9-4 | 12-3 | 15-5 | 17-10 | 9-1 | 11-6 | 14-1 | 16-3
| Spruce-Pine-Fir | #2 | 9-4 | 12-3 | 15-5 | 17-10 | 9-1 | 11-6 | 14-1 | 16-3
| Spruce-Pine-Fir | #3 | 7-6 | 9-6 | 11-8 | 13-6 | 6-10 | 8-8 | 10-7 | 12-4
24 | Douglas Fir-Larch | SS | 9-1 | 11-11 | 15-2 | 18-5 | 9-1 | 11-11 | 14-9 | 17-1
| Douglas Fir-Larch | #1 | 8-8 | 11-1 | 13-5 | 15-7 | 7-11 | 10-1 | 12-3 | 14-3
| Douglas Fir-Larch | #2 | 8-1 | 10-3 | 12-7 | 14-7 | 7-5 | 9-5 | 11-6 | 13-4
| Douglas Fir-Larch | #3 | 6-2 | 7-9 | 9-6 | 11-1 | 5-7 | 7-1 | 8-8 | 10-1
| Hem-Fir | SS | 8-6 | 11-3 | 14-4 | 17-5 | 8-6 | 11-3 | 14-4 | 16-10
| Hem-Fir | #1 | 8-4 | 10-9 | 13-1 | 15-2 | 7-9 | 9-9 | 11-11 | 13-10
| Hem-Fir | #2 | 7-11 | 10-2 | 12-5 | 14-4 | 7-4 | 9-3 | 11-4 | 13-1
| Hem-Fir | #3 | 6-2 | 7-9 | 9-6 | 11-1 | 5-7 | 7-1 | 8-8 | 10-1
| Southern Pine | SS | 8-10 | 11-8 | 14-11 | 18-1 | 8-10 | 11-8 | 14-11 | 18-0
| Southern Pine | #1 | 8-6 | 11-3 | 13-1 | 15-7 | 8-1 | 10-3 | 12-1 | 14-3
| Southern Pine | #2 | 7-7 | 9-8 | 11-5 | 13-6 | 7-1 | 8-10 | 10-5 | 12-4
| Southern Pine | #3 | 5-9 | 7-3 | 8-10 | 10-5 | 5-3 | 6-8 | 8-1 | 9-6
| Spruce-Pine-Fir | SS | 8-4 | 11-1 | 14-0 | 17-0 | 8-4 | 11-1 | 13-8 | 15-11
| Spruce-Pine-Fir | #1 | 8-1 | 10-3 | 12-7 | 14-7 | 7-5 | 9-5 | 11-6 | 13-4
| Spruce-Pine-Fir | #2 | 8-1 | 10-3 | 12-7 | 14-7 | 7-5 | 9-5 | 11-6 | 13-4
| Spruce-Pine-Fir | #3 | 6-2 | 7-9 | 9-6 | 11-1 | 5-7 | 7-1 | 8-8 | 10-1

## 2308.5.1
TABLE 2308.5.1
SIZE, HEIGHT AND SPACING OF WOOD STUDSc
| BEARING WALLS |  |  |  | NONBEARING WALLS
| Laterally unsupported stud heighta (feet) | Supporting roof and ceiling only | Supporting one floor, roof and ceiling | Supporting two floors, roof and ceiling | Laterally unsupported stud heighta (feet) | Spacing (inches)
Spacing (inches)
2 × 3b | — | — | — | — | 10 | 16
2 × 4 | 10 | 24 | 16 | — | 14 | 24
3 × 4 | 10 | 24 | 24 | 16 | 14 | 24
2 × 5 | 10 | 24 | 24 | — | 16 | 24
2 × 6 | 10 | 24 | 24 | 16 | 20 | 24

## 2308.5.11
TABLE 2308.5.11
MINIMUM THICKNESS OF WALL SHEATHING
SHEATHING TYPE | MINIMUM THICKNESS | MAXIMUM WALL STUD SPACING
Diagonal wood boards | 5/8 inch | 24 inches on center
Structural fiberboard | 1/2 inch | 16 inches on center
Wood structural panel | In accordance with Tables 2308.6.3(2) and 2308.6.3(3) | —
M-S "Exterior Glue" and M-2 "Exterior Glue" particleboard | In accordance with Section 2306.3 and Table 2308.6.3(4) | —
Gypsum sheathing | 1/2 inch | 16 inches on center
Reinforced cement mortar | 1 inch | 24 inches on center
Hardboard panel siding | In accordance with Table 2308.6.3(5) | —

## 2308.6.1a
TABLE 2308.6.1a
WALL BRACING REQUIREMENTS
|  |  | BRACED PANEL LOCATION, SPACING (O.C.) AND MINIMUM PERCENTAGE (X) |  |  | MAXIMUM DISTANCE OF BRACED WALL PANELS FROM EACH END OF BRACED WALL LINE
SEISMIC DESIGN CATEGORY | STORY CONDITION (SEE SECTION 2308.2) | MAXIMUM SPACING OF BRACED WALL LINES | Bracing methodb
|  |  | LIB | DWB, WSP | SFB, PBS, PCP, HPS, GBc, d
A and B |  | 35'- 0" | Each end and ≤ 25'- 0" o.c. | Each end and ≤ 25'- 0" o.c. | Each end and ≤ 25'- 0" o.c. | 12'- 6"
|  | 35'- 0" | Each end and ≤ 25'- 0" o.c. | Each end and ≤ 25'- 0" o.c. | Each end and ≤ 25'- 0" o.c. | 12'- 6"
|  | 35'- 0" | NP | Each end and ≤ 25'- 0" o.c. | Each end and ≤ 25'- 0" o.c. | 12'- 6"
C |  | 35'- 0" | NP | Each end and ≤ 25'- 0" o.c. | Each end and ≤ 25'- 0" o.c. | 12'- 6"
|  | 35'- 0" | NP | Each end and ≤ 25'- 0" o.c. (minimum 25% of wall length)c | Each end and ≤ 25'- 0" o.c. (minimum 25% of wall length)c | 12'- 6"
D |  | 25'- 0" | NP | SDS < 0.50: Each end and ≤ 25'- 0" o.c. (minimum 21% of wall length)c | SDS < 0.50: Each end and ≤ 25'- 0" o.c. (minimum 43% of wall length)c | 8'- 0"
|  |  |  | 0.5 ≤ SDS < 0.75: Each end and ≤ 25'- 0" o.c. (minimum 32% of wall length)c | 0.5 ≤ SDS < 0.75: Each end and ≤ 25'- 0" o.c. (minimum 59% of wall length)c
|  |  |  | 0.75 ≤ SDS ≤ 1.00: Each end and ≤ 25'- 0" o.c. (minimum 37% of wall length)c | 0.75 ≤ SDS ≤ 1.00: Each end and ≤ 25'- 0" o.c. (minimum 75% of wall length)
|  |  |  | SDS > 1.00: Each end and ≤ 25'- 0" o.c. (minimum 48% of wall length)c | SDS > 1.00: Each end and ≤ 25'- 0" o.c. (minimum 100% of wall length)c

## 2308.6.3(1)
TABLE 2308.6.3(1)
BRACING METHODS
METHODS, MATERIAL | MINIMUM THICKNESS | FIGURE | CONNECTION CRITERIAa
|  |  | Fasteners | Spacing
LIBa Let-in-bracing | 1" × 4" wood or approved metal straps attached at 45° to 60° angles to studs at maximum of 16" o.c. | [Figure - image] | Table 2304.10.1 | Wood: per stud plus top and bottom plates
|  |  | Metal strap: installed in accordance with manufacturer's recommendations | Metal strap: installed in accordance with manufacturer's recommendations
DWB Diagonal wood boards | 3/4" thick (1" nominal) × 6" minimum width to studs at maximum of 24" o.c. | [Figure - image] | Table 2304.10.1 | Per stud
WSP Wood structural panel | 3/8" in accordance with Table 2308.6.3(2) or 2308.6.3(3) | [Figure - image] | Table 2304.10.1 | 6" edges 12" field
SFB Structural fiberboard sheathing | 1/2" in accordance with Table 2304.10.2 to studs at maximum 16" o.c. | [Figure - image] | Table 2304.10.1 | 3" edges 6" field
GB Gypsum board (Double sided) | 1/2" or 5/8" by not less than 4" wide to studs at maximum of 24" o.c. | [Figure - image] | Section 2506.2 for exterior and interior sheathing: 5d annual ringed cooler nails (1-5/8" × 0.086") or 1-1/4" screws (Type W or S) for 1/2" gypsum board or 1-5/8" screws (Type W or S) for 5/8" gypsum board | For all braced wall panel locations: 7" o.c. along panel edges (including top and bottom plates) and 7" o.c. in the field
PBS Particleboard sheathing | 3/8" or 1/2" in accordance with Table 2308.6.3(4) to studs at maximum of 16" o.c. | [Figure - image] | 6d common (2" long × 0.113" dia.) nails for 3/8" thick sheathing or 8d common (2-1/2" long × 0.131" dia.) nails for 1/2" thick sheathing | 3" edges 6" field
PCP Portland cement plaster | Section 2510 to studs at maximum of 16" o.c. | [Figure - image] | 1-1/2" long, 11 gage, 7/16" dia. head nails or 7/8" long, 16 gage staples | 6" o.c. on all framing members
HPS Hardboard panel siding | 7/16" in accordance with Table 2308.6.3(5) | [Figure - image] | Table 2304.10.1 | 4" edges 8" field
ABW Alternate braced wall | 3/8" | [Figure - image] | Figure 2308.6.5.1 and Section 2308.6.5.1 | Figure 2308.6.5.1
PFH Portal frame with hold-downs | 3/8" | [Figure - image] | Figure 2308.6.5.2 and Section 2308.6.5.2 | Figure 2308.6.5.2

## 2308.6.3(2)
TABLE 2308.6.3(2)
EXPOSED PLYWOOD PANEL SIDING
MINIMUM THICKNESSa (inch) | MINIMUM NUMBER OF PLIES | STUD SPACING (inches) Plywood siding applied directly to studs or over sheathing
2026-03-08 | 3 | 16b
2026-01-02 | 4 | 24

## 2308.6.3(3)
TABLE 2308.6.3(3)
WOOD STRUCTURAL PANEL WALL SHEATHINGb
(Not exposed to the weather, strength axis parallel or perpendicular to studs except as indicated)
MINIMUM THICKNESS (inch) | PANEL SPAN RATING | STUD SPACING (inches)
|  | Siding nailed to studs | Nailable sheathing
|  |  | Sheathing parallel to studs | Sheathing perpendicular to studs
3/8, 15/32, 1/2 | 16/0, 20/0, 24/0, 32/16 Wall—24" o.c. | 24 | 16 | 24
7/16, 15/32, 1/2 | 24/0, 24/16, 32/16 Wall—24" o.c. | 24 | 24a | 24

## 2308.6.3(4)
TABLE 2308.6.3(4)
ALLOWABLE SPANS FOR PARTICLEBOARD WALL SHEATHING
(Not exposed to the weather, long dimension of the panel parallel or perpendicular to studs)
GRADE | THICKNESS (inch) | STUD SPACING (inches)
|  | Siding nailed to studs | Sheathing under coverings specified in Section 2308.6.3 parallel or perpendicular to studs
M-S “Exterior Glue” and M-2 “Exterior Glue” | 2026-03-08 | 16 | —
| 2026-01-02 | 16 | 16

## 2308.6.3(5)
TABLE 2308.6.3(5)
HARDBOARD SIDING
SIDING | MINIMUM NOMINAL THICKNESS (inch) | 2 × 4 FRAMING MAXIMUM SPACING | NAIL SIZEa, b, d | NAIL SPACING
|  |  |  | General | Bracing panelsc
1. Lap siding
Direct to studs | 2026-03-08 | 16" o.c. | 8d | 16" o.c. | Not applicable
Over sheathing | 2026-03-08 | 16" o.c. | 10d | 16" o.c. | Not applicable
2. Square edge panel siding
Direct to studs | 2026-03-08 | 24" o.c. | 6d | 6" o.c. edges; 12" o.c. at intermediate supports | 4" o.c. edges; 8" o.c. at intermediate supports
Over sheathing | 2026-03-08 | 24" o.c. | 8d | 6" o.c. edges; 12" o.c. at intermediate supports | 4" o.c. edges; 8" o.c. at intermediate supports
3. Shiplap edge panel siding
Direct to studs | 2026-03-08 | 16" o.c. | 6d | 6" o.c. edges; 12" o.c. at intermediate supports | 4" o.c. edges; 8" o.c. at intermediate supports
Over sheathing | 2026-03-08 | 16" o.c. | 8d | 6" o.c. edges; 12" o.c. at intermediate supports | 4" o.c. edges; 8" o.c. at intermediate supports

## NAIL DIMENSIONS
| Panel Siding (inch) | Lap Siding (inch)
Shank diameter | 0.092 | 0.099
Head diameter | 0.225 | 0.24

## 2308.7.1(1)
TABLE 2308.7.1(1) — CEILING JOIST SPANS FOR COMMON LUMBER SPECIES
Uninhabitable attics without storage, live load = 10 psf, L/Δ = 240
DEAD LOAD = 5 psf
CEILING JOIST SPACING (inches) | SPECIES | GRADE | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10
|  |  | Maximum ceiling joist spans (ft. – in.) | Maximum ceiling joist spans (ft. – in.) | Maximum ceiling joist spans (ft. – in.) | Maximum ceiling joist spans (ft. – in.)
12 | Douglas Fir-Larch | SS | 13-2 | 20-8 | Note a | Note a
12 | Douglas Fir-Larch | #1 | 12-8 | 19-11 | Note a | Note a
12 | Douglas Fir-Larch | #2 | 12-5 | 19-6 | 25-8 | Note a
12 | Douglas Fir-Larch | #3 | 10-10 | 15-10 | 20-1 | 24-6
12 | Hem-Fir | SS | 12-5 | 19-6 | 25-8 | Note a
12 | Hem-Fir | #1 | 12-2 | 19-1 | 25-2 | Note a
12 | Hem-Fir | #2 | 11-7 | 18-2 | 24-0 | Note a
12 | Hem-Fir | #3 | 10-10 | 15-10 | 20-1 | 24-6
12 | Southern Pine | SS | 12-11 | 20-3 | Note a | Note a
12 | Southern Pine | #1 | 12-5 | 19-6 | 25-8 | Note a
12 | Southern Pine | #2 | 11-10 | 18-8 | 24-7 | Note a
12 | Southern Pine | #3 | 10-1 | 14-11 | 18-9 | 22-9
12 | Spruce-Pine-Fir | SS | 12-2 | 19-1 | 25-2 | Note a
12 | Spruce-Pine-Fir | #1 | 11-10 | 18-8 | 24-7 | Note a
12 | Spruce-Pine-Fir | #2 | 11-10 | 18-8 | 24-7 | Note a
12 | Spruce-Pine-Fir | #3 | 10-10 | 15-10 | 20-1 | 24-6
16 | Douglas Fir-Larch | SS | 11-11 | 18-9 | 24-8 | Note a
16 | Douglas Fir-Larch | #1 | 11-6 | 18-1 | 23-10 | Note a
16 | Douglas Fir-Larch | #2 | 11-3 | 17-8 | 23-0 | Note a
16 | Douglas Fir-Larch | #3 | 9-5 | 13-9 | 17-5 | 21-3
16 | Hem-Fir | SS | 11-3 | 17-8 | 23-4 | Note a
16 | Hem-Fir | #1 | 11-0 | 17-4 | 22-10 | Note a
16 | Hem-Fir | #2 | 10-6 | 16-6 | 21-9 | Note a
16 | Hem-Fir | #3 | 9-5 | 13-9 | 17-5 | 21-3
16 | Southern Pine | SS | 11-9 | 18-5 | 24-3 | Note a
16 | Southern Pine | #1 | 11-3 | 17-8 | 23-4 | Note a
16 | Southern Pine | #2 | 10-9 | 16-11 | 21-7 | 25-7
16 | Southern Pine | #3 | 8-9 | 12-11 | 16-3 | 19-9
16 | Spruce-Pine-Fir | SS | 11-0 | 17-4 | 22-10 | Note a
16 | Spruce-Pine-Fir | #1 | 10-9 | 16-11 | 22-4 | Note a
16 | Spruce-Pine-Fir | #2 | 10-9 | 16-11 | 22-4 | Note a
16 | Spruce-Pine-Fir | #3 | 9-5 | 13-9 | 17-5 | 21-3
19.2 | Douglas Fir-Larch | SS | 11-3 | 17-8 | 23-3 | Note a
19.2 | Douglas Fir-Larch | #1 | 10-10 | 17-0 | 22-5 | Note a
19.2 | Douglas Fir-Larch | #2 | 10-7 | 16-7 | 21-0 | 25-8
19.2 | Douglas Fir-Larch | #3 | 8-7 | 12-6 | 15-10 | 19-5
19.2 | Hem-Fir | SS | 10-7 | 16-8 | 21-11 | Note a
19.2 | Hem-Fir | #1 | 10-4 | 16-4 | 21-6 | Note a
19.2 | Hem-Fir | #2 | 9-11 | 15-7 | 20-6 | 25-3
19.2 | Hem-Fir | #3 | 8-7 | 12-6 | 15-10 | 19-5
19.2 | Southern Pine | SS | 11-0 | 17-4 | 22-10 | Note a
19.2 | Southern Pine | #1 | 10-7 | 16-8 | 22-0 | Note a
19.2 | Southern Pine | #2 | 10-2 | 15-7 | 19-8 | 23-5
19.2 | Southern Pine | #3 | 8-0 | 11-9 | 14-10 | 18-0
19.2 | Spruce-Pine-Fir | SS | 10-4 | 16-4 | 21-6 | Note a
19.2 | Spruce-Pine-Fir | #1 | 10-2 | 15-11 | 21-0 | 25-8
19.2 | Spruce-Pine-Fir | #2 | 10-2 | 15-11 | 21-0 | 25-8
19.2 | Spruce-Pine-Fir | #3 | 8-7 | 12-6 | 15-10 | 19-5
24 | Douglas Fir-Larch | SS | 10-5 | 16-4 | 21-7 | Note a
24 | Douglas Fir-Larch | #1 | 10-0 | 15-9 | 20-1 | 24-6
24 | Douglas Fir-Larch | #2 | 9-10 | 14-10 | 18-9 | 22-11
24 | Douglas Fir-Larch | #3 | 7-8 | 11-2 | 14-2 | 17-4
24 | Hem-Fir | SS | 9-10 | 15-6 | 20-5 | Note a
24 | Hem-Fir | #1 | 9-8 | 15-2 | 19-7 | 23-11
24 | Hem-Fir | #2 | 9-2 | 14-5 | 18-6 | 22-7
24 | Hem-Fir | #3 | 7-8 | 11-2 | 14-2 | 17-4
24 | Southern Pine | SS | 10-3 | 16-1 | 21-2 | Note a
24 | Southern Pine | #1 | 9-10 | 15-6 | 20-5 | 24-0
24 | Southern Pine | #2 | 9-3 | 13-11 | 17-7 | 20-11
24 | Southern Pine | #3 | 7-2 | 10-6 | 13-3 | 16-1
24 | Spruce-Pine-Fir | SS | 9-8 | 15-2 | 19-11 | 25-5
24 | Spruce-Pine-Fir | #1 | 9-5 | 14-9 | 18-9 | 22-11
24 | Spruce-Pine-Fir | #2 | 9-5 | 14-9 | 18-9 | 22-11
24 | Spruce-Pine-Fir | #3 | 7-8 | 11-2 | 14-2 | 17-4

## 2308.7.1(2)
TABLE 2308.7.1(2) — CEILING JOIST SPANS FOR COMMON LUMBER SPECIES
Uninhabitable attics with limited storage, live load = 20 psf, L/Δ = 240
DEAD LOAD = 10 psf
CEILING JOIST SPACING (inches) | SPECIES | GRADE | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10
|  |  | Maximum ceiling joist spans (ft. – in.) | Maximum ceiling joist spans (ft. – in.) | Maximum ceiling joist spans (ft. – in.) | Maximum ceiling joist spans (ft. – in.)
12 | Douglas Fir-Larch | SS | 10-5 | 16-4 | 21-7 | Note a
12 | Douglas Fir-Larch | #1 | 10-0 | 15-9 | 20-1 | 24-6
12 | Douglas Fir-Larch | #2 | 9-10 | 14-10 | 18-9 | 22-11
12 | Douglas Fir-Larch | #3 | 7-8 | 11-2 | 14-2 | 17-4
12 | Hem-Fir | SS | 9-10 | 15-6 | 20-5 | Note a
12 | Hem-Fir | #1 | 9-8 | 15-2 | 19-7 | 23-11
12 | Hem-Fir | #2 | 9-2 | 14-5 | 18-6 | 22-7
12 | Hem-Fir | #3 | 7-8 | 11-2 | 14-2 | 17-4
12 | Southern Pine | SS | 10-3 | 16-1 | 21-2 | Note a
12 | Southern Pine | #1 | 9-10 | 15-6 | 20-5 | 24-0
12 | Southern Pine | #2 | 9-3 | 13-11 | 17-7 | 20-11
12 | Southern Pine | #3 | 7-2 | 10-6 | 13-3 | 16-1
12 | Spruce-Pine-Fir | SS | 9-8 | 15-2 | 19-11 | 25-5
12 | Spruce-Pine-Fir | #1 | 9-5 | 14-9 | 18-9 | 22-11
12 | Spruce-Pine-Fir | #2 | 9-5 | 14-9 | 18-9 | 22-11
12 | Spruce-Pine-Fir | #3 | 7-8 | 11-2 | 14-2 | 17-4
16 | Douglas Fir-Larch | SS | 9-6 | 14-11 | 19-7 | 25-0
16 | Douglas Fir-Larch | #1 | 9-1 | 13-9 | 17-5 | 21-3
16 | Douglas Fir-Larch | #2 | 8-9 | 12-10 | 16-3 | 19-10
16 | Douglas Fir-Larch | #3 | 6-8 | 9-8 | 12-4 | 15-0
16 | Hem-Fir | SS | 8-11 | 14-1 | 18-6 | 23-8
16 | Hem-Fir | #1 | 8-9 | 13-5 | 16-10 | 20-8
16 | Hem-Fir | #2 | 8-4 | 12-8 | 16-0 | 19-7
16 | Hem-Fir | #3 | 6-8 | 9-8 | 12-4 | 15-0
16 | Southern Pine | SS | 9-4 | 14-7 | 19-3 | 24-7
16 | Southern Pine | #1 | 8-11 | 14-0 | 17-9 | 20-9
16 | Southern Pine | #2 | 8-0 | 12-0 | 15-3 | 18-1
16 | Southern Pine | #3 | 6-2 | 9-2 | 11-6 | 14-0
16 | Spruce-Pine-Fir | SS | 8-9 | 13-9 | 18-1 | 23-1
16 | Spruce-Pine-Fir | #1 | 8-7 | 12-10 | 16-3 | 19-10
16 | Spruce-Pine-Fir | #2 | 8-7 | 12-10 | 16-3 | 19-10
16 | Spruce-Pine-Fir | #3 | 6-8 | 9-8 | 12-4 | 15-0
19.2 | Douglas Fir-Larch | SS | 8-11 | 14-0 | 18-5 | 23-4
19.2 | Douglas Fir-Larch | #1 | 8-7 | 12-6 | 15-10 | 19-5
19.2 | Douglas Fir-Larch | #2 | 8-0 | 11-9 | 14-10 | 18-2
19.2 | Douglas Fir-Larch | #3 | 6-1 | 8-10 | 11-3 | 13-8
19.2 | Hem-Fir | SS | 8-5 | 13-3 | 17-5 | 22-3
19.2 | Hem-Fir | #1 | 8-3 | 12-3 | 15-6 | 18-11
19.2 | Hem-Fir | #2 | 7-10 | 11-7 | 14-8 | 17-10
19.2 | Hem-Fir | #3 | 6-1 | 8-10 | 11-3 | 13-8
19.2 | Southern Pine | SS | 8-9 | 13-9 | 18-2 | 23-1
19.2 | Southern Pine | #1 | 8-5 | 12-9 | 16-2 | 18-11
19.2 | Southern Pine | #2 | 7-4 | 11-0 | 13-11 | 16-6
19.2 | Southern Pine | #3 | 5-8 | 8-4 | 10-6 | 12-9
19.2 | Spruce-Pine-Fir | SS | 8-3 | 12-11 | 17-1 | 21-8
19.2 | Spruce-Pine-Fir | #1 | 8-0 | 11-9 | 14-10 | 18-2
19.2 | Spruce-Pine-Fir | #2 | 8-0 | 11-9 | 14-10 | 18-2
19.2 | Spruce-Pine-Fir | #3 | 6-1 | 8-10 | 11-3 | 13-8
24 | Douglas Fir-Larch | SS | 8-3 | 13-0 | 17-1 | 20-11
24 | Douglas Fir-Larch | #1 | 7-8 | 11-2 | 14-2 | 17-4
24 | Douglas Fir-Larch | #2 | 7-2 | 10-6 | 13-3 | 16-3
24 | Douglas Fir-Larch | #3 | 5-5 | 7-11 | 10-0 | 12-3
24 | Hem-Fir | SS | 7-10 | 12-3 | 16-2 | 20-6
24 | Hem-Fir | #1 | 7-6 | 10-11 | 13-10 | 16-11
24 | Hem-Fir | #2 | 7-1 | 10-4 | 13-1 | 16-0
24 | Hem-Fir | #3 | 5-5 | 7-11 | 10-0 | 12-3
24 | Southern Pine | SS | 8-1 | 12-9 | 16-10 | 21-6
24 | Southern Pine | #1 | 7-8 | 11-5 | 14-6 | 16-11
24 | Southern Pine | #2 | 6-7 | 9-10 | 12-6 | 14-9
24 | Southern Pine | #3 | 5-1 | 7-5 | 9-5 | 11-5
24 | Spruce-Pine-Fir | SS | 7-8 | 12-0 | 15-10 | 19-5
24 | Spruce-Pine-Fir | #1 | 7-2 | 10-6 | 13-3 | 16-3
24 | Spruce-Pine-Fir | #2 | 7-2 | 10-6 | 13-3 | 16-3
24 | Spruce-Pine-Fir | #3 | 5-5 | 7-11 | 10-0 | 12-3

## 2308.7.2(1)
TABLE 2308.7.2(1) — RAFTER SPANS FOR COMMON LUMBER SPECIES
Roof live load = 20 psf, ceiling not attached to rafters, L/Δ = 180
|  |  | DEAD LOAD = 10 psf |  |  |  |  | DEAD LOAD = 20 psf
RAFTER SPACING (inches) | SPECIES | GRADE | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12 | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12
|  |  | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.) | Maximum rafter spans (ft. – in.)
12 | Douglas Fir-Larch | SS | 11-6 | 18-0 | 23-9 | Note b | Note b | 11-6 | 18-0 | 23-5 | Note b | Note b
12 | Douglas Fir-Larch | #1 | 11-1 | 17-4 | 22-5 | Note b | Note b | 10-6 | 15-4 | 15-4 | 23-9 | Note b
12 | Douglas Fir-Larch | #2 | 10-10 | 16-7 | 21-0 | 25-8 | Note b | 9-10 | 14-4 | 18-2 | 22-3 | 25-9
12 | Douglas Fir-Larch | #3 | 8-7 | 12-6 | 15-10 | 19-5 | 22-6 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6
12 | Hem-Fir | SS | 10-10 | 17-0 | 22-5 | Note b | Note b | 10-10 | 17-0 | 22-5 | Note b | Note b
12 | Hem-Fir | #1 | 10-7 | 16-8 | 21-10 | Note b | Note b | 10-3 | 14-11 | 18-11 | 23-2 | Note b
12 | Hem-Fir | #2 | 10-1 | 15-11 | 20-8 | 25-3 | Note b | 9-8 | 14-2 | 17-11 | 21-11 | 25-5
12 | Hem-Fir | #3 | 8-7 | 12-6 | 15-10 | 19-5 | 22-6 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6
12 | Southern Pine | SS | 11-3 | 17-8 | 23-4 | Note b | Note b | 11-3 | 17-8 | 23-4 | Note b | Note b
12 | Southern Pine | #1 | 10-10 | 17-0 | 22-5 | 26-0 | 26-0 | 10-6 | 15-8 | 19-10 | 23-2 | Note b
12 | Southern Pine | #2 | 10-4 | 15-7 | 19-8 | 23-5 | 26-0 | 9-0 | 13-6 | 17-1 | 20-3 | 23-10
12 | Southern Pine | #3 | 8-0 | 11-9 | 14-10 | 18-0 | 21-4 | 6-11 | 10-2 | 12-10 | 15-7 | 18-6
12 | Spruce-Pine-Fir | SS | 10-7 | 16-8 | 21-11 | Note b | Note b | 10-7 | 16-8 | 21-9 | Note b | Note b
12 | Spruce-Pine-Fir | #1 | 10-4 | 16-3 | 21-0 | 25-8 | Note b | 9-10 | 14-4 | 18-2 | 22-3 | 25-9
12 | Spruce-Pine-Fir | #2 | 10-4 | 16-3 | 21-0 | 25-8 | Note b | 9-10 | 14-4 | 18-2 | 22-3 | 25-9
12 | Spruce-Pine-Fir | #3 | 8-7 | 12-6 | 15-10 | 19-5 | 22-6 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6
16 | Douglas Fir-Larch | SS | 10-5 | 16-4 | 21-7 | Note b | Note b | 10-5 | 16-0 | 20-3 | 24-9 | Note b
16 | Douglas Fir-Larch | #1 | 10-0 | 15-4 | 19-5 | 23-9 | Note b | 9-1 | 13-3 | 16-10 | 20-7 | 23-10
16 | Douglas Fir-Larch | #2 | 9-10 | 14-4 | 18-2 | 22-3 | 25-9 | 8-6 | 12-5 | 15-9 | 19-3 | 22-4
16 | Douglas Fir-Larch | #3 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6 | 6-5 | 9-5 | 11-11 | 14-6 | 16-10
16 | Hem-Fir | SS | 9-10 | 15-6 | 20-5 | Note b | Note b | 9-10 | 15-6 | 19-11 | 24-4 | Note b
16 | Hem-Fir | #1 | 9-8 | 14-11 | 18-11 | 23-2 | Note b | 8-10 | 12-11 | 16-5 | 20-0 | 23-3
16 | Hem-Fir | #2 | 9-2 | 14-2 | 17-11 | 21-11 | 25-5 | 8-5 | 12-3 | 15-6 | 18-11 | 22-0
16 | Hem-Fir | #3 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6 | 6-5 | 9-5 | 11-11 | 14-6 | 16-10
16 | Southern Pine | SS | 10-3 | 16-1 | 21-2 | Note b | Note b | 10-3 | 16-1 | 21-2 | 25-7 | Note b
16 | Southern Pine | #1 | 9-10 | 15-6 | 19-10 | 23-2 | 26-0 | 9-1 | 13-7 | 17-2 | 20-1 | 23-10
16 | Southern Pine | #2 | 9-0 | 13-6 | 17-1 | 20-3 | 23-10 | 7-9 | 11-8 | 14-9 | 17-6 | 20-8
16 | Southern Pine | #3 | 6-11 | 10-2 | 12-10 | 15-7 | 18-6 | 6-0 | 8-10 | 11-2 | 13-6 | 16-0
16 | Spruce-Pine-Fir | SS | 9-8 | 15-2 | 19-11 | 25-5 | Note b | 9-8 | 14-10 | 18-10 | 23-0 | Note b
16 | Spruce-Pine-Fir | #1 | 9-5 | 14-4 | 18-2 | 22-3 | 25-9 | 8-6 | 12-5 | 15-9 | 19-3 | 22-4
16 | Spruce-Pine-Fir | #2 | 9-5 | 14-4 | 18-2 | 22-3 | 25-9 | 8-6 | 12-5 | 15-9 | 19-3 | 22-4
16 | Spruce-Pine-Fir | #3 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6 | 6-5 | 9-5 | 11-11 | 14-6 | 16-10
19.2 | Douglas Fir-Larch | SS | 9-10 | 15-5 | 20-4 | 25-11 | Note b | 9-10 | 14-7 | 18-6 | 22-7 | Note b
19.2 | Douglas Fir-Larch | #1 | 9-5 | 14-0 | 17-9 | 21-8 | 25-2 | 8-4 | 12-2 | 15-4 | 18-9 | 21-9
19.2 | Douglas Fir-Larch | #2 | 8-11 | 13-1 | 16-7 | 20-3 | 23-6 | 7-9 | 11-4 | 14-4 | 17-7 | 20-4
19.2 | Douglas Fir-Larch | #3 | 6-9 | 9-11 | 12-7 | 15-4 | 17-9 | 5-10 | 8-7 | 10-10 | 13-3 | 15-5
19.2 | Hem-Fir | SS | 9-3 | 14-7 | 19-2 | 24-6 | Note b | 9-3 | 14-4 | 18-2 | 22-3 | 25-9
19.2 | Hem-Fir | #1 | 9-1 | 13-8 | 17-4 | 21-1 | 24-6 | 8-1 | 11-10 | 15-0 | 18-4 | 21-3
19.2 | Hem-Fir | #2 | 8-8 | 12-11 | 16-4 | 20-0 | 23-2 | 7-8 | 11-2 | 14-2 | 17-4 | 20-1
19.2 | Hem-Fir | #3 | 6-9 | 9-11 | 12-7 | 15-4 | 17-9 | 5-10 | 8-7 | 10-10 | 13-3 | 15-5
19.2 | Southern Pine | SS | 9-8 | 15-2 | 19-11 | 25-5 | Note b | 9-8 | 15-2 | 19-11 | 23-4 | Note b
19.2 | Southern Pine | #1 | 9-3 | 14-3 | 18-1 | 21-2 | 25-2 | 8-4 | 12-4 | 15-8 | 18-4 | 21-9
19.2 | Southern Pine | #2 | 8-2 | 12-3 | 15-7 | 18-6 | 21-9 | 7-1 | 10-8 | 13-6 | 16-0 | 18-10
19.2 | Southern Pine | #3 | 6-4 | 9-4 | 11-9 | 14-3 | 16-10 | 5-6 | 8-1 | 10-2 | 12-4 | 14-7
19.2 | Spruce-Pine-Fir | SS | 9-1 | 14-3 | 18-9 | 23-11 | Note b | 9-1 | 13-7 | 17-2 | 21-0 | 24-4
19.2 | Spruce-Pine-Fir | #1 | 8-10 | 13-1 | 16-7 | 20-3 | 23-6 | 7-9 | 11-4 | 14-4 | 17-7 | 20-4
19.2 | Spruce-Pine-Fir | #2 | 8-10 | 13-1 | 16-7 | 20-3 | 23-6 | 7-9 | 11-4 | 14-4 | 17-7 | 20-4
19.2 | Spruce-Pine-Fir | #3 | 6-9 | 9-11 | 12-7 | 15-4 | 17-9 | 5-10 | 8-7 | 10-10 | 13-3 | 15-5
24 | Douglas Fir-Larch | SS | 9-1 | 14-4 | 18-10 | 23-4 | Note b | 8-11 | 13-1 | 16-7 | 20-3 | 23-5
24 | Douglas Fir-Larch | #1 | 8-7 | 12-6 | 15-10 | 19-5 | 22-6 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6
24 | Douglas Fir-Larch | #2 | 8-0 | 11-9 | 14-10 | 18-2 | 21-0 | 6-11 | 10-2 | 12-10 | 15-8 | 18-3
24 | Douglas Fir-Larch | #3 | 6-1 | 8-10 | 11-3 | 13-8 | 15-11 | 5-3 | 7-8 | 9-9 | 11-10 | 13-9
24 | Hem-Fir | SS | 8-7 | 13-6 | 17-10 | 22-9 | Note b | 8-7 | 12-10 | 16-3 | 19-10 | 23-0
24 | Hem-Fir | #1 | 8-4 | 12-3 | 15-6 | 18-11 | 21-11 | 7-3 | 10-7 | 13-5 | 16-4 | 19-0
24 | Hem-Fir | #2 | 7-11 | 11-7 | 14-8 | 17-10 | 20-9 | 6-10 | 10-0 | 12-8 | 15-6 | 17-11
24 | Hem-Fir | #3 | 6-1 | 8-10 | 11-3 | 13-8 | 15-11 | 5-3 | 7-8 | 9-9 | 11-10 | 13-9
24 | Southern Pine | SS | 8-11 | 14-1 | 18-6 | 23-8 | Note b | 8-11 | 14-1 | 18-6 | 22-11 | Note b
24 | Southern Pine | #1 | 8-7 | 12-9 | 16-2 | 18-11 | 22-6 | 7-5 | 11-1 | 14-0 | 16-5 | 19-6
24 | Southern Pine | #2 | 7-4 | 11-0 | 13-11 | 16-6 | 19-6 | 6-4 | 9-6 | 12-1 | 14-4 | 16-10
24 | Southern Pine | #3 | 5-8 | 8-4 | 10-6 | 12-9 | 15-1 | 4-11 | 7-3 | 9-1 | 11-0 | 13-1
24 | Spruce-Pine-Fir | SS | 8-5 | 13-3 | 17-5 | 21-8 | 25-2 | 8-4 | 12-2 | 15-4 | 18-9 | 21-9
24 | Spruce-Pine-Fir | #1 | 8-0 | 11-9 | 14-10 | 18-2 | 21-0 | 6-11 | 10-2 | 12-10 | 15-8 | 18-3
24 | Spruce-Pine-Fir | #2 | 8-0 | 11-9 | 14-10 | 18-2 | 21-0 | 6-11 | 10-2 | 12-10 | 15-8 | 18-3
24 | Spruce-Pine-Fir | #3 | 6-1 | 8-10 | 11-3 | 13-8 | 15-11 | 5-3 | 7-8 | 9-9 | 11-10 | 13-9

## RAFTER SPAN
Hc/HR | Rafter Span Adjustment Factor
1/3 | 0.67
1/4 | 0.76
1/5 | 0.83
1/6 | 0.9
1/7.5 or less | 1

## 2308.7.2(2)
TABLE 2308.7.2(2) — RAFTER SPANS FOR COMMON LUMBER SPECIES
Roof live load = 20 psf, Ceiling Attached to Rafters, L/Δ = 240
|  |  | DEAD LOAD = 10 psf |  |  |  |  | DEAD LOAD = 20 psf
RAFTER SPACING (inches) | SPECIES AND GRADE |  | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12 | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12
Maximum rafter spans
|  |  | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.)
12 | Douglas Fir-Larch | SS | 10-5 | 16-4 | 21-7 | Note b | Note b | 10-5 | 16-4 | 21-7 | Note b | Note b
| Douglas Fir-Larch | #1 | 10-0 | 15-9 | 20-10 | Note b | Note b | 10-0 | 15-4 | 19-5 | 23-9 | Note b
| Douglas Fir-Larch | #2 | 9-10 | 15-6 | 20-5 | 25-8 | Note b | 9-10 | 14-4 | 18-2 | 22-3 | 25-9
| Douglas Fir-Larch | #3 | 8-7 | 12-6 | 15-10 | 19-5 | 22-6 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6
| Hem-Fir | SS | 9-10 | 15-6 | 20-5 | Note b | Note b | 9-10 | 15-6 | 20-5 | Note b | Note b
| Hem-Fir | #1 | 9-8 | 15-2 | 19-11 | 25-5 | Note b | 9-8 | 14-11 | 18-11 | 23-2 | Note b
| Hem-Fir | #2 | 9-2 | 14-5 | 19-0 | 24-3 | Note b | 9-2 | 14-2 | 17-11 | 21-11 | 25-5
| Hem-Fir | #3 | 8-7 | 12-6 | 15-10 | 19-5 | 22-6 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6
| Southern Pine | SS | 10-3 | 16-1 | 21-2 | Note b | Note b | 10-3 | 16-1 | 21-2 | Note b | Note b
| Southern Pine | #1 | 9-10 | 15-6 | 20-5 | 26-0 | 26-0 | 9-10 | 15-6 | 19-10 | 23-2 | 26-0
| Southern Pine | #2 | 9-5 | 14-9 | 19-6 | 23-5 | 26-0 | 9-0 | 13-6 | 17-1 | 20-3 | 23-10
| Southern Pine | #3 | 8-0 | 11-9 | 14-10 | 18-0 | 21-4 | 6-11 | 10-2 | 12-10 | 15-7 | 18-6
| Spruce-Pine-Fir | SS | 9-8 | 15-2 | 19-11 | 25-5 | Note b | 9-8 | 15-2 | 19-11 | 25-5 | Note b
| Spruce-Pine-Fir | #1 | 9-5 | 14-9 | 19-6 | 24-10 | Note b | 9-5 | 14-4 | 18-2 | 22-3 | 25-9
| Spruce-Pine-Fir | #2 | 9-5 | 14-9 | 19-6 | 24-10 | Note b | 9-5 | 14-4 | 18-2 | 22-3 | 25-9
| Spruce-Pine-Fir | #3 | 8-7 | 12-6 | 15-10 | 19-5 | 22-6 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6
16 | Douglas Fir-Larch | SS | 9-6 | 14-11 | 19-7 | 25-0 | Note b | 9-6 | 14-11 | 19-7 | 24-9 | Note b
| Douglas Fir-Larch | #1 | 9-1 | 14-4 | 18-11 | 23-9 | Note b | 9-1 | 13-3 | 16-10 | 20-7 | 23-10
| Douglas Fir-Larch | #2 | 8-11 | 14-1 | 18-2 | 22-3 | 25-9 | 8-6 | 12-5 | 15-9 | 19-3 | 22-4
| Douglas Fir-Larch | #3 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6 | 6-5 | 9-5 | 11-11 | 14-6 | 16-10
| Hem-Fir | SS | 8-11 | 14-1 | 18-6 | 23-8 | Note b | 8-11 | 14-1 | 18-6 | 23-8 | Note b
| Hem-Fir | #1 | 8-9 | 13-9 | 18-1 | 23-1 | Note b | 8-9 | 12-11 | 16-5 | 20-0 | 23-3
| Hem-Fir | #2 | 8-4 | 13-1 | 17-3 | 21-11 | 25-5 | 8-4 | 12-3 | 15-6 | 18-11 | 22-0
| Hem-Fir | #3 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6 | 6-5 | 9-5 | 11-11 | 14-6 | 16-10
| Southern Pine | SS | 9-4 | 14-7 | 19-3 | 24-7 | Note b | 9-4 | 14-7 | 19-3 | 24-7 | Note b
| Southern Pine | #1 | 8-11 | 14-1 | 18-6 | 23-2 | 26-0 | 8-11 | 13-7 | 17-2 | 20-1 | 23-10
| Southern Pine | #2 | 8-7 | 13-5 | 17-1 | 20-3 | 23-10 | 7-9 | 11-8 | 14-9 | 17-6 | 20-8
| Southern Pine | #3 | 6-11 | 10-2 | 12-10 | 15-7 | 18-6 | 6-0 | 8-10 | 11-2 | 13-6 | 16-0
| Spruce-Pine-Fir | SS | 8-9 | 13-9 | 18-1 | 23-1 | Note b | 8-9 | 13-9 | 18-1 | 23-0 | Note b
| Spruce-Pine-Fir | #1 | 8-7 | 13-5 | 17-9 | 22-3 | 25-9 | 8-6 | 12-5 | 15-9 | 19-3 | 22-4
| Spruce-Pine-Fir | #2 | 8-7 | 13-5 | 17-9 | 22-3 | 25-9 | 8-6 | 12-5 | 15-9 | 19-3 | 22-4
| Spruce-Pine-Fir | #3 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6 | 6-5 | 9-5 | 11-11 | 14-6 | 16-10
19.2 | Douglas Fir-Larch | SS | 8-11 | 14-0 | 18-5 | 23-7 | Note b | 8-11 | 14-0 | 18-5 | 22-7 | Note b
| Douglas Fir-Larch | #1 | 8-7 | 13-6 | 17-9 | 21-8 | 25-2 | 8-4 | 12-2 | 15-4 | 18-9 | 21-9
| Douglas Fir-Larch | #2 | 8-5 | 13-1 | 16-7 | 20-3 | 23-6 | 7-9 | 11-4 | 14-4 | 17-3 | 20-4
| Douglas Fir-Larch | #3 | 6-9 | 9-11 | 12-7 | 15-4 | 17-9 | 5-10 | 8-7 | 10-10 | 13-3 | 15-5
| Hem-Fir | SS | 8-5 | 13-3 | 17-5 | 22-3 | Note b | 8-5 | 13-3 | 17-5 | 22-3 | 25-9
| Hem-Fir | #1 | 8-3 | 12-11 | 17-1 | 21-1 | 24-6 | 8-1 | 11-10 | 15-0 | 18-4 | 21-3
| Hem-Fir | #2 | 7-10 | 12-4 | 16-3 | 20-0 | 23-2 | 7-8 | 11-2 | 14-2 | 17-4 | 20-1
| Hem-Fir | #3 | 6-9 | 9-11 | 12-7 | 15-4 | 17-9 | 5-10 | 8-7 | 10-10 | 13-3 | 15-5
| Southern Pine | SS | 8-9 | 13-9 | 18-2 | 23-1 | Note b | 8-9 | 13-9 | 18-2 | 23-1 | Note b
| Southern Pine | #1‡ | 8-5 | 13-3 | 17-5 | 21-2 | 25-2 | 8-4 | 12-4 | 15-8 | 18-4 | 21-9
| Southern Pine | #2‡ | 8-1 | 12-3 | 15-7 | 18-6 | 21-9 | 7-1 | 10-8 | 13-6 | 16-0 | 18-10
| Southern Pine | #3‡ | 6-4 | 9-4 | 11-9 | 14-3 | 16-10 | 5-6 | 8-1 | 10-2 | 12-4 | 14-7
| Spruce-Pine-Fir | SS | 8-3 | 12-11 | 17-1 | 21-9 | Note b | 8-3 | 12-11 | 17-1 | 21-0 | 24-4
| Spruce-Pine-Fir | #1 | 8-1 | 12-8 | 16-7 | 20-3 | 23-6 | 7-9 | 11-4 | 14-4 | 17-7 | 20-4
| Spruce-Pine-Fir | #2 | 8-1 | 12-8 | 16-7 | 20-3 | 23-6 | 7-9 | 11-4 | 14-4 | 17-7 | 20-4
| Spruce-Pine-Fir | #3 | 6-9 | 9-11 | 12-7 | 15-4 | 17-9 | 5-10 | 8-7 | 10-10 | 13-3 | 15-5
24 | Douglas Fir-Larch | SS | 8-3 | 13-0 | 17-2 | 21-10 | Note b | 8-3 | 13-0 | 16-7 | 20-3 | 23-5
| Douglas Fir-Larch | #1 | 8-0 | 12-6 | 15-10 | 19-5 | 22-6 | 7-5 | 10-10 | 13-9 | 16-9 | 19-6
| Douglas Fir-Larch | #2 | 7-10 | 11-9 | 14-10 | 18-2 | 21-0 | 6-11 | 10-2 | 12-10 | 15-8 | 18-3
| Douglas Fir-Larch | #3 | 6-1 | 8-10 | 11-3 | 13-8 | 15-11 | 5-3 | 7-8 | 9-9 | 11-10 | 13-9
| Hem-Fir | SS | 7-10 | 12-3 | 16-2 | 20-8 | 25-1 | 7-10 | 12-3 | 16-2 | 19-10 | 23-0
| Hem-Fir | #1 | 7-8 | 12-0 | 15-6 | 18-11 | 21-11 | 7-3 | 10-7 | 13-5 | 16-4 | 19-0
| Hem-Fir | #2 | 7-3 | 11-5 | 14-8 | 17-10 | 20-9 | 6-10 | 10-0 | 12-8 | 15-6 | 17-11
| Hem-Fir | #3 | 6-1 | 8-10 | 11-3 | 13-8 | 15-11 | 5-3 | 7-8 | 9-9 | 11-10 | 13-9
| Southern Pine | SS | 8-1 | 12-9 | 16-10 | 21-6 | Note b | 8-1 | 12-9 | 16-10 | 21-6 | Note b
| Southern Pine | #1‡ | 7-10 | 12-3 | 16-2 | 18-11 | 22-6 | 7-5 | 11-1 | 14-0 | 16-5 | 19-6
| Southern Pine | #2‡ | 7-4 | 11-0 | 13-11 | 16-6 | 19-6 | 6-4 | 9-6 | 12-1 | 14-4 | 16-10
| Southern Pine | #3‡ | 5-8 | 8-4 | 10-6 | 12-9 | 15-1 | 4-11 | 7-3 | 9-1 | 11-0 | 13-1
| Spruce-Pine-Fir | SS | 7-8 | 12-0 | 15-10 | 20-2 | 24-7 | 7-8 | 12-0 | 15-4 | 18-9 | 21-9
| Spruce-Pine-Fir | #1 | 7-6 | 11-9 | 14-10 | 18-2 | 21-0 | 6-11 | 10-2 | 12-10 | 15-8 | 18-3
| Spruce-Pine-Fir | #2 | 7-6 | 11-9 | 14-10 | 18-2 | 21-0 | 6-11 | 10-2 | 12-10 | 15-8 | 18-3
| Spruce-Pine-Fir | #3 | 6-1 | 8-10 | 11-3 | 13-8 | 15-11 | 5-3 | 7-8 | 9-9 | 11-10 | 13-9

## 2308.7.2(3)
TABLE 2308.7.2(3)
RAFTER SPANS FOR COMMON LUMBER SPECIES
(Ground snow load = 30 psf, Ceiling Not Attached to Rafters, L/Δ = 180)
1/5 | 0.83 |  | DEAD LOAD = 10 psf |  |  |  |  | DEAD LOAD = 20 psf
RAFTER SPACING (inches) | SPECIES AND GRADE |  | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12 | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12
Maximum rafter spanss
|  |  | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.)
12 | Douglas Fir-Larch | SS | 10-0 | 15-9 | 20-9 | Note b | Note b | 10-0 | 15-9 | 20-1 | 24-6 | Note b
| Douglas Fir-Larch | #1 | 9-8 | 14-9 | 18-8 | 22-9 | Note b | 9-0 | 13-2 | 16-8 | 20-4 | 23-7
| Douglas Fir-Larch | #2 | 9-5 | 13-9 | 17-5 | 21-4 | 24-8 | 8-5 | 12-4 | 15-7 | 19-1 | 22-1
| Douglas Fir-Larch | #3 | 7-1 | 10-5 | 13-2 | 16-1 | 18-8 | 6-4 | 9-4 | 11-9 | 14-5 | 16-8
| Hem-Fir | SS | 9-6 | 14-10 | 19-7 | 25-0 | Note b | 9-6 | 14-10 | 19-7 | 24-1 | Note b
| Hem-Fir | #1 | 9-3 | 14-4 | 18-2 | 22-2 | 25-9 | 8-9 | 12-10 | 16-3 | 19-10 | 23-0
| Hem-Fir | #2 | 8-10 | 13-7 | 17-2 | 21-0 | 24-4 | 8-4 | 12-2 | 15-4 | 18-9 | 21-9
| Hem-Fir | #3 | 7-1 | 10-5 | 13-2 | 16-1 | 18-8 | 6-4 | 9-4 | 11-9 | 14-5 | 16-8
| Southern Pine | SS | 9-10 | 15-6 | 20-5 | Note b | Note b | 9-10 | 15-6 | 20-5 | Note b | Note b
| Southern Pine | #1 | 9-6 | 14-10 | 19-0 | 22-3 | 26-0 | 9-0 | 13-5 | 17-0 | 19-11 | 23-7
| Southern Pine | #2 | 8-7 | 12-11 | 16-4 | 19-5 | 22-10 | 7-8 | 11-7 | 14-8 | 17-4 | 20-5
| Southern Pine | #3 | 6-7 | 9-9 | 12-4 | 15-0 | 17-9 | 5-11 | 8-9 | 11-0 | 13-5 | 15-10
| Spruce-Pine-Fir | SS | 9-3 | 14-7 | 19-2 | 24-6 | Note b | 9-3 | 14-7 | 18-8 | 22-9 | Note b
| Spruce-Pine-Fir | #1 | 9-1 | 13-9 | 17-5 | 21-4 | 24-8 | 8-5 | 12-4 | 15-7 | 19-1 | 22-1
| Spruce-Pine-Fir | #2 | 9-1 | 13-9 | 17-5 | 21-4 | 24-8 | 8-5 | 12-4 | 15-7 | 19-1 | 22-1
| Spruce-Pine-Fir | #3 | 7-1 | 10-5 | 13-2 | 16-1 | 18-8 | 6-4 | 9-4 | 11-9 | 14-5 | 16-8
16 | Douglas Fir-Larch | SS | 9-1 | 14-4 | 18-10 | 23-9 | Note b | 9-1 | 13-9 | 17-5 | 21-3 | 24-8
| Douglas Fir-Larch | #1 | 8-9 | 12-9 | 16-2 | 19-9 | 22-10 | 7-10 | 11-5 | 14-5 | 17-8 | 20-5
| Douglas Fir-Larch | #2 | 8-2 | 11-11 | 15-1 | 18-5 | 21-5 | 7-3 | 10-8 | 13-6 | 16-6 | 19-2
| Douglas Fir-Larch | #3 | 6-2 | 9-0 | 11-5 | 13-11 | 16-2 | 5-6 | 8-1 | 10-3 | 12-6 | 14-6
| Hem-Fir | SS | 8-7 | 13-6 | 17-10 | 22-9 | Note b | 8-7 | 13-6 | 17-1 | 20-10 | 24-2
| Hem-Fir | #1 | 8-5 | 12-5 | 15-9 | 19-3 | 22-3 | 7-7 | 11-1 | 14-1 | 17-2 | 19-11
| Hem-Fir | #2 | 8-0 | 11-9 | 14-11 | 18-2 | 21-1 | 7-2 | 10-6 | 13-4 | 16-3 | 18-10
| Hem-Fir | #3 | 6-2 | 9-0 | 11-5 | 13-11 | 16-2 | 5-6 | 8-1 | 10-3 | 12-6 | 14-6
| Southern Pine | SS | 8-11 | 14-1 | 18-6 | 23-8 | Note b | 8-11 | 14-1 | 18-6 | 23-8 | Note b
| Southern Pine | #1 | 8-7 | 13-0 | 16-6 | 19-3 | 22-10 | 7-10 | 11-7 | 14-9 | 17-3 | 20-5
| Southern Pine | #2 | 7-6 | 11-2 | 14-2 | 16-10 | 19-10 | 6-8 | 10-0 | 12-8 | 15-1 | 17-9
| Southern Pine | #3 | 5-9 | 8-6 | 10-8 | 13-0 | 15-4 | 5-2 | 7-7 | 9-7 | 11-7 | 13-9
| Spruce-Pine-Fir | SS | 8-5 | 13-3 | 17-5 | 22-1 | 25-7 | 8-5 | 12-9 | 16-2 | 19-9 | 22-10
| Spruce-Pine-Fir | #1 | 8-2 | 11-11 | 15-1 | 18-5 | 21-5 | 7-2 | 10-8 | 13-6 | 16-6 | 19-2
| Spruce-Pine-Fir | #2 | 8-2 | 11-11 | 15-1 | 18-5 | 21-5 | 7-3 | 10-8 | 13-6 | 16-6 | 19-2
| Spruce-Pine-Fir | #3 | 6-2 | 9-0 | 11-5 | 13-11 | 16-2 | 5-6 | 8-1 | 10-3 | 12-6 | 14-6
19.2 | Douglas Fir-Larch | SS | 8-7 | 13-6 | 17-9 | 21-8 | 25-2 | 8-7 | 12-6 | 15-10 | 19-5 | 22-6
| Douglas Fir-Larch | #1 | 7-11 | 11-8 | 14-9 | 18-0 | 20-11 | 7-1 | 10-5 | 13-2 | 16-1 | 18-8
| Douglas Fir-Larch | #2 | 7-5 | 10-11 | 13-9 | 16-10 | 19-6 | 6-8 | 9-9 | 12-4 | 15-1 | 17-6
| Douglas Fir-Larch | #3 | 5-7 | 8-3 | 10-5 | 12-9 | 14-9 | 5-0 | 7-4 | 9-4 | 11-5 | 13-2
| Hem-Fir | SS | 8-1 | 12-9 | 16-9 | 21-4 | 24-8 | 8-1 | 12-4 | 15-7 | 19-1 | 22-1
| Hem-Fir | #1 | 7-9 | 11-4 | 14-4 | 17-7 | 20-4 | 6-11 | 10-2 | 12-10 | 15-8 | 18-2
| Hem-Fir | #2 | 7-4 | 10-9 | 13-7 | 16-7 | 19-3 | 6-7 | 9-7 | 12-2 | 14-10 | 17-3
| Hem-Fir | #3 | 5-7 | 8-3 | 10-5 | 12-9 | 14-9 | 5-0 | 7-4 | 9-4 | 11-5 | 13-2
| Southern Pine | SS | 8-5 | 13-3 | 17-5 | 22-3 | Note b | 8-5 | 13-3 | 17-5 | 22-0 | 25-9
| Southern Pine | #1‡ | 8-0 | 11-10 | 15-1 | 17-7 | 20-11 | 7-1 | 10-7 | 13-5 | 15-9 | 18-8
| Southern Pine | #2‡ | 6-10 | 10-2 | 12-11 | 15-4 | 18-1 | 6-1 | 9-2 | 11-7 | 13-9 | 16-2
| Southern Pine | #3‡ | 5-3 | 7-9 | 9-9 | 11-10 | 14-0 | 4-8 | 6-11 | 8-9 | 10-7 | 12-6
| Spruce-Pine-Fir | SS | 7-11 | 12-5 | 16-5 | 20-2 | 23-4 | 7-11 | 11-8 | 14-9 | 18-0 | 20-11
| Spruce-Pine-Fir | #1 | 7-5 | 10-11 | 13-9 | 16-10 | 19-6 | 6-8 | 9-9 | 12-4 | 15-1 | 17-6
| Spruce-Pine-Fir | #2 | 7-5 | 10-11 | 13-9 | 16-10 | 19-6 | 6-8 | 9-9 | 12-4 | 15-1 | 17-6
| Spruce-Pine-Fir | #3 | 5-7 | 8-3 | 10-5 | 12-9 | 14-9 | 5-0 | 7-4 | 9-4 | 11-5 | 13-2
24 | Douglas Fir-Larch | SS | 7-11 | 12-6 | 15-10 | 19-5 | 22-6 | 7-8 | 11-3 | 14-2 | 17-4 | 20-1
| Douglas Fir-Larch | #1 | 7-1 | 10-5 | 13-2 | 16-1 | 18-8 | 6-4 | 9-4 | 11-9 | 14-5 | 16-8
| Douglas Fir-Larch | #2 | 6-8 | 9-9 | 12-4 | 15-1 | 17-6 | 5-11 | 8-8 | 11-0 | 13-6 | 15-7
| Douglas Fir-Larch | #3 | 5-0 | 7-4 | 9-4 | 11-5 | 13-2 | 4-6 | 6-7 | 8-4 | 10-2 | 11-10
| Hem-Fir | SS | 7-6 | 11-10 | 15-7 | 19-1 | 22-1 | 7-6 | 11-0 | 13-11 | 17-0 | 19-9
| Hem-Fir | #1 | 6-11 | 10-2 | 12-10 | 15-8 | 18-2 | 6-2 | 9-1 | 11-6 | 14-0 | 16-3
| Hem-Fir | #2 | 6-7 | 9-7 | 12-2 | 14-10 | 17-3 | 5-10 | 8-7 | 10-10 | 13-3 | 15-5
| Hem-Fir | #3 | 5-0 | 7-4 | 9-4 | 11-5 | 13-2 | 4-6 | 6-7 | 8-4 | 10-2 | 11-10
| Southern Pine | SS | 7-10 | 12-3 | 16-2 | 20-8 | 25-1 | 7-10 | 12-3 | 16-2 | 19-8 | 23-0
| Southern Pine | #1 | 7-1 | 10-7 | 13-5 | 15-9 | 18-8 | 6-4 | 9-6 | 12-0 | 14-1 | 16-8
| Southern Pine | #2 | 6-1 | 9-2 | 11-7 | 13-9 | 16-2 | 5-5 | 8-2 | 10-4 | 12-3 | 14-6
| Southern Pine | #3 | 4-8 | 6-11 | 8-9 | 10-7 | 12-6 | 4-2 | 6-2 | 7-10 | 9-6 | 11-2
| Spruce-Pine-Fir | SS | 7-4 | 11-7 | 14-9 | 18-0 | 20-11 | 7-1 | 10-5 | 13-2 | 16-1 | 18-8
| Spruce-Pine-Fir | #1 | 6-8 | 9-9 | 12-4 | 15-1 | 17-6 | 5-11 | 8-8 | 11-0 | 13-6 | 15-7
| Spruce-Pine-Fir | #2 | 6-8 | 9-9 | 12-4 | 15-1 | 17-6 | 5-11 | 8-8 | 11-0 | 13-6 | 15-7
| Spruce-Pine-Fir | #3 | 5-0 | 7-4 | 9-4 | 11-5 | 13-2 | 4-6 | 6-7 | 8-4 | 10-2 | 11-10

## 2308.7.2(4)
TABLE 2308.7.2(4)
RAFTER SPANS FOR COMMON LUMBER SPECIES
(Ground snow load = 50 psf, Ceiling Not Attached to Rafters, L/Δ = 180)
|  |  | DEAD LOAD = 10 psf |  |  |  |  | DEAD LOAD = 20 psf
RAFTER SPACING (inches) | SPECIES AND GRADE |  | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12 | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12
Maximum rafter spansᵃ
|  |  | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.)
12 | Douglas Fir-Larch | SS | 2026-08-05 | 13-3 | 17-6 | 22-4 | 26-0 | 2026-08-05 | 13-3 | 17-0 | 20-9 | 24-10
| Douglas Fir-larch | #1 | 2026-08-02 | 2000-12-01 | 15-3 | 18-7 | 21-7 | 2026-07-07 | 2026-11-02 | 14-1 | 17-3 | 20-0
| Douglas Fir-larch | #2 | 2026-07-08 | 2026-11-03 | 14-3 | 17-5 | 20-2 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Douglas Fir-larch | #3 | 2026-05-10 | 2026-08-06 | 2026-10-09 | 13-2 | 15-3 | 2026-05-05 | 2026-07-10 | 2000-10-01 | 2026-12-02 | 14-1
| Hem-Fir | SS | 2000-08-01 | 2026-12-06 | 16-6 | 21-1 | 25-6 | 2000-08-01 | 2026-12-06 | 16-6 | 20-4 | 23-7
| Hem-Fir | #1 | 2026-07-10 | 2026-11-09 | 14-10 | 18-1 | 21-0 | 2026-07-05 | 2026-10-10 | 13-9 | 16-9 | 19-5
| Hem-Fir | #2 | 2026-07-05 | 2026-11-01 | 14-0 | 17-2 | 19-11 | 2000-07-01 | 2026-10-03 | 13-0 | 15-10 | 18-5
| Hem-Fir | #3 | 2026-05-10 | 2026-08-06 | 2026-10-09 | 13-2 | 15-3 | 2026-05-05 | 2026-07-10 | 2000-10-01 | 2026-12-02 | 14-1
| Southern Pine | SS‡ | 2026-08-04 | 13-1 | 17-2 | 21-11 | Note b | 2026-08-04 | 13-1 | 17-2 | 21-5 | 25-3
| Southern Pine | #1‡ | 2000-08-01 | 2026-12-03 | 15-6 | 18-2 | 21-7 | 2026-07-07 | 2026-11-04 | 14-5 | 16-10 | 20-0
| Southern Pine | #2‡ | 2000-07-01 | 2026-10-06 | 13-4 | 15-10 | 18-8 | 2026-06-06 | 2026-09-09 | 2026-12-04 | 14-8 | 17-3
| Southern Pine | #3‡ | 2026-05-05 | 2000-08-01 | 2026-10-01 | 2026-12-03 | 14-6 | 2000-05-01 | 2026-07-05 | 2026-09-04 | 2026-11-04 | 13-5
| Spruce-Pine-Fir | SS | 2026-07-10 | 2026-12-03 | 16-2 | 20-8 | 24-1 | 2026-07-10 | 2026-12-03 | 15-9 | 19-3 | 22-4
| Spruce-Pine-Fir | #1 | 2026-07-08 | 2026-11-03 | 14-3 | 17-5 | 20-2 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Spruce-Pine-Fir | #2 | 2026-07-08 | 2026-11-03 | 14-3 | 17-5 | 20-2 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Spruce-Pine-Fir | #3 | 2026-05-10 | 2026-08-06 | 2026-10-09 | 13-2 | 15-3 | 2026-05-05 | 2026-07-10 | 2000-10-01 | 2026-12-02 | 14-1
16 | Douglas Fir-Larch | SS | 2026-07-08 | 2026-12-01 | 15-10 | 19-5 | 22-6 | 2026-07-08 | 2026-11-07 | 14-8 | 17-11 | 20-10
| Douglas Fir-Larch | #1 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8 | 2026-06-07 | 2026-09-08 | 2026-12-02 | 14-11 | 17-3
| Douglas Fir-Larch | #2 | 2026-06-08 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2
| Douglas Fir-Larch | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-08 | 2026-06-10 | 2026-08-08 | 2026-10-06 | 2026-12-03
| Hem-Fir | SS | 2026-07-03 | 2026-11-05 | 15-0 | 19-1 | 22-1 | 2026-07-03 | 2026-11-05 | 14-5 | 17-8 | 20-5
| Hem-Fir | #1 | 2026-06-11 | 2026-10-02 | 2026-12-10 | 15-8 | 18-2 | 2026-06-05 | 2026-09-05 | 2026-11-11 | 14-6 | 16-10
| Hem-Fir | #2 | 2026-06-07 | 2026-09-07 | 2026-12-02 | 14-10 | 17-3 | 2026-06-01 | 2026-08-11 | 2026-11-03 | 13-9 | 15-11
| Hem-Fir | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-08 | 2026-06-10 | 2026-08-08 | 2026-10-06 | 2026-12-03
| Southern Pine | SS | 2026-07-06 | 2026-11-10 | 15-7 | 19-11 | 23-7 | 2026-07-06 | 2026-11-10 | 15-7 | 18-6 | 21-10
| Southern Pine | #1‡ | 2026-07-01 | 2026-10-07 | 13-5 | 15-9 | 18-8 | 2026-06-07 | 2026-09-10 | 2026-12-05 | 14-7 | 17-3
| Southern Pine | #2‡ | 2026-06-01 | 2026-09-02 | 2026-11-07 | 13-9 | 16-2 | 2026-05-08 | 2026-08-05 | 2026-10-09 | 2026-12-09 | 15-0
| Southern Pine | #3‡ | 2026-04-08 | 2026-06-11 | 2026-08-09 | 2026-10-07 | 2026-12-06 | 2026-04-04 | 2026-06-05 | 2026-08-01 | 2026-09-10 | 2026-11-07
| Spruce-Pine-Fir | SS | 2026-07-01 | 2026-11-02 | 14-8 | 18-0 | 20-11 | 2026-07-01 | 2026-10-09 | 13-8 | 15-11 | 19-4
| Spruce-Pine-Fir | #1 | 2026-06-08 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2
| Spruce-Pine-Fir | #2 | 2026-06-08 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2
| Spruce-Pine-Fir | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-08 | 2026-06-10 | 2026-08-08 | 2026-10-06 | 2026-12-03
19.2 | Douglas Fir-Larch | SS | 2026-07-03 | 2026-11-04 | 14-6 | 17-8 | 20-6 | 2026-07-03 | 2026-10-07 | 13-5 | 16-5 | 19-0
| Douglas Fir-Larch | #1 | 2026-06-06 | 2026-09-06 | 2000-12-01 | 14-8 | 17-1 | 2000-06-01 | 2026-08-10 | 2026-11-02 | 13-7 | 15-9
| Douglas Fir-Larch | #2 | 2026-06-01 | 2026-08-11 | 2026-11-03 | 13-9 | 15-11 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9
| Douglas Fir-Larch | #3 | 2026-04-07 | 2026-06-09 | 2026-08-06 | 2026-10-05 | 2026-12-01 | 2026-04-03 | 2026-06-03 | 2026-07-11 | 2026-09-07 | 2026-11-02
| Hem-Fir | SS | 2026-06-10 | 2026-10-09 | 14-2 | 17-5 | 20-2 | 2026-06-10 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Hem-Fir | #1 | 2026-06-04 | 2026-09-03 | 2026-11-09 | 14-4 | 16-7 | 2026-05-10 | 2026-08-07 | 2026-10-10 | 13-3 | 15-5
| Hem-Fir | #2 | 2000-06-01 | 2026-08-09 | 2026-11-01 | 13-7 | 15-9 | 2026-05-07 | 2026-08-01 | 2026-10-03 | 2026-12-07 | 14-7
| Hem-Fir | #3 | 2026-04-07 | 2026-06-09 | 2026-08-06 | 2026-10-05 | 2026-12-01 | 2026-04-03 | 2026-06-03 | 2026-07-11 | 2026-09-07 | 2026-11-02
| Southern Pine | SS | 2026-07-01 | 2026-11-02 | 14-8 | 18-3 | 21-7 | 2026-07-01 | 2026-11-02 | 14-2 | 16-11 | 20-0
| Southern Pine | #1‡ | 2026-06-06 | 2026-09-08 | 2026-12-03 | 14-4 | 17-1 | 2000-06-01 | 2000-09-01 | 2026-11-04 | 13-4 | 15-9
| Southern Pine | #2‡ | 2026-05-07 | 2026-08-04 | 2026-10-07 | 2026-12-06 | 14-9 | 2026-05-02 | 2026-07-09 | 2026-09-09 | 2026-11-07 | 13-8
| Southern Pine | #3‡ | 2026-04-03 | 2026-06-04 | 2000-08-01 | 2026-09-08 | 2026-11-05 | 2000-04-01 | 2026-05-10 | 2026-07-04 | 2026-08-11 | 2026-10-07
| Spruce-Pine-Fir | SS | 2026-06-08 | 2026-10-06 | 13-5 | 16-5 | 19-1 | 2026-06-08 | 2026-09-10 | 2026-12-05 | 15-3 | 17-8
| Spruce-Pine-Fir | #1 | 2026-06-01 | 2026-08-11 | 2026-11-03 | 13-9 | 15-11 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9
| Spruce-Pine-Fir | #2 | 2026-06-01 | 2026-08-11 | 2026-11-03 | 13-9 | 15-11 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9
| Spruce-Pine-Fir | #3 | 2026-04-07 | 2026-06-09 | 2026-08-06 | 2026-10-05 | 2026-12-01 | 2026-04-03 | 2026-06-03 | 2026-07-11 | 2026-09-07 | 2026-11-02
24 | Douglas Fir-Larch | SS | 2026-06-08 | 2026-10-03 | 13-0 | 15-10 | 18-4 | 2026-06-06 | 2026-09-06 | 2000-12-01 | 14-8 | 17-0
| Douglas Fir-Larch | #1 | 2026-05-10 | 2026-08-06 | 2026-10-09 | 13-2 | 15-3 | 2026-05-05 | 2026-07-10 | 2000-10-01 | 2026-12-02 | 14-1
| Douglas Fir-Larch | #2 | 2026-05-05 | 2026-07-11 | 2026-10-01 | 2026-12-04 | 14-3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
| Douglas Fir-Larch | #3 | 2026-04-01 | 2000-06-01 | 2026-07-07 | 2026-09-04 | 2026-10-09 | 2026-03-10 | 2026-05-07 | 2026-07-01 | 2026-08-07 | 2000-10-01
| Hem-Fir | SS | 2026-06-04 | 2026-09-11 | 2026-12-09 | 15-7 | 18-0 | 2026-06-04 | 2026-09-04 | 2026-11-09 | 14-5 | 16-8
| Hem-Fir | #1 | 2026-05-08 | 2026-08-03 | 2026-10-06 | 2026-12-10 | 14-10 | 2026-05-03 | 2026-07-08 | 2026-09-09 | 2026-11-10 | 13-9
| Hem-Fir | #2 | 2026-05-04 | 2026-07-10 | 2026-09-11 | 2026-12-01 | 14-1 | 2026-04-11 | 2026-07-03 | 2026-09-02 | 2026-11-03 | 13-0
| Hem-Fir | #3 | 2026-04-01 | 2000-06-01 | 2026-07-07 | 2026-09-04 | 2026-10-09 | 2026-03-10 | 2026-05-07 | 2026-07-01 | 2026-08-07 | 2000-10-01
| Southern Pine | SS‡ | 2026-06-07 | 2026-10-04 | 13-8 | 16-4 | 19-3 | 2026-06-07 | 2000-10-01 | 2026-12-08 | 15-2 | 17-10
| Southern Pine | #1‡ | 2026-05-10 | 2026-08-08 | 2000-11-01 | 2026-12-10 | 15-3 | 2026-05-05 | 2000-08-01 | 2026-10-02 | 2026-11-11 | 14-1
| Southern Pine | #2‡ | 2000-05-01 | 2026-07-05 | 2026-09-05 | 2026-11-03 | 13-2 | 2026-04-07 | 2026-06-11 | 2026-08-09 | 2026-10-05 | 2026-12-03
| Southern Pine | #3‡ | 2026-03-10 | 2026-05-08 | 2026-07-01 | 2026-08-08 | 2026-10-03 | 2026-03-06 | 2026-05-03 | 2026-06-07 | 2000-08-01 | 2026-09-06
| Spruce-Pine-Fir | SS | 2026-06-02 | 2026-09-06 | 2000-12-01 | 14-8 | 17-1 | 2000-06-01 | 2026-08-10 | 2026-11-02 | 13-7 | 15-9
| Spruce-Pine-Fir | #1 | 2026-05-05 | 2026-07-11 | 2026-10-01 | 2026-12-04 | 14-3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
| Spruce-Pine-Fir | #2 | 2026-05-05 | 2026-07-11 | 2026-10-01 | 2026-12-04 | 14-3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
| Spruce-Pine-Fir | #3 | 2026-04-01 | 2000-06-01 | 2026-07-07 | 2026-09-04 | 2026-10-09 | 2026-03-10 | 2026-05-07 | 2026-07-01 | 2026-08-07 | 2000-10-01

## 2308.7.2(5)
TABLE 2308.7.2(5)
RAFTER SPANS FOR COMMON LUMBER SPECIES
(Ground snow load = 30 psf, Ceiling Attached to Rafters, L/Δ = 240)
|  |  | DEAD LOAD = 10 psf |  |  |  |  | DEAD LOAD = 20 psf
RAFTER SPACING (inches) | SPECIES AND GRADE |  | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12 | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12
Maximum rafter spansᵃ
|  |  | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.)
12 | Douglas Fir-Larch | SS | 2026-09-01 | 14-4 | 18-10 | 24-1 | Note b | 2026-09-01 | 14-4 | 18-10 | 24-1 | Note b
| Douglas Fir-Larch | #1 | 2026-08-09 | 13-9 | 18-2 | 22-9 | Note b | 2026-08-09 | 13-2 | 16-8 | 20-4 | 23-7
| Douglas Fir-Larch | #2 | 2026-08-07 | 13-6 | 17-5 | 21-4 | 24-8 | 2026-08-05 | 2026-12-04 | 15-7 | 19-1 | 22-1
| Douglas Fir-Larch | #3 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8 | 2026-06-04 | 2026-09-04 | 2026-11-09 | 14-5 | 16-8
| Hem-Fir | SS | 2026-08-07 | 13-6 | 17-10 | 22-9 | Note b | 2026-08-07 | 13-6 | 17-10 | 22-9 | Note b
| Hem-Fir | #1 | 2026-08-05 | 13-3 | 17-5 | 22-2 | 25-9 | 2026-08-05 | 2026-12-10 | 16-3 | 19-10 | 23-0
| Hem-Fir | #2 | 2000-08-01 | 2026-12-07 | 16-7 | 21-0 | 24-4 | 2000-08-01 | 2026-12-02 | 15-4 | 18-9 | 21-9
| Hem-Fir | #3 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8 | 2026-06-04 | 2026-09-04 | 2026-11-09 | 14-5 | 16-8
| Southern Pine | SS | 2026-08-11 | 14-1 | 18-6 | 23-8 | Note b | 2026-08-11 | 14-1 | 18-6 | 23-8 | Note b
| Southern Pine | #1 | 2026-08-07 | 13-6 | 17-10 | 22-3 | Note b | 2026-08-07 | 13-5 | 17-0 | 19-11 | 23-7
| Southern Pine | #2 | 2026-08-03 | 2026-12-11 | 16-4 | 19-5 | 22-10 | 2026-07-08 | 2026-11-07 | 14-8 | 17-4 | 20-5
| Southern Pine | #3 | 2026-06-07 | 2026-09-09 | 2026-12-04 | 15-0 | 17-9 | 2026-05-11 | 2026-08-09 | 2000-11-01 | 13-5 | 15-10
| Spruce-Pine-Fir | SS | 2026-08-05 | 13-3 | 17-5 | 22-3 | Note b | 2026-08-05 | 13-3 | 17-5 | 22-3 | Note b
| Spruce-Pine-Fir | #1 | 2026-08-03 | 2026-12-11 | 17-0 | 21-4 | 24-8 | 2026-08-03 | 2026-12-04 | 15-7 | 19-1 | 22-1
| Spruce-Pine-Fir | #2 | 2026-08-03 | 2026-12-11 | 17-0 | 21-4 | 24-8 | 2026-08-03 | 2026-12-04 | 15-7 | 19-1 | 22-1
| Spruce-Pine-Fir | #3 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8 | 2026-06-04 | 2026-09-04 | 2026-11-09 | 14-5 | 16-8
16 | Douglas Fir-Larch | SS | 2026-08-03 | 13-0 | 17-2 | 21-10 | Note b | 2026-08-03 | 13-0 | 17-2 | 21-3 | 24-8
| Douglas Fir-Larch | #1 | 2000-08-01 | 2026-12-06 | 16-2 | 19-9 | 22-10 | 2026-07-10 | 2026-11-05 | 14-5 | 17-8 | 20-5
| Douglas Fir-Larch | #2 | 2026-07-10 | 2026-11-11 | 15-1 | 18-5 | 21-5 | 2026-07-03 | 2026-10-08 | 13-6 | 16-6 | 19-2
| Douglas Fir-Larch | #3 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2 | 2026-05-06 | 2026-08-01 | 2026-10-03 | 2026-12-06 | 14-6
| Hem-Fir | SS | 2026-07-10 | 2026-12-03 | 16-2 | 20-8 | 25-1 | 2026-07-10 | 2026-12-03 | 16-2 | 20-8 | 24-2
| Hem-Fir | #1 | 2026-07-08 | 2000-12-01 | 15-9 | 19-3 | 22-3 | 2026-07-07 | 2026-11-01 | 14-1 | 17-2 | 19-11
| Hem-Fir | #2 | 2026-07-03 | 2026-11-05 | 14-11 | 18-2 | 21-1 | 2026-07-02 | 2026-10-06 | 13-4 | 16-3 | 18-10
| Hem-Fir | #3 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2 | 2026-05-06 | 2026-08-01 | 2026-10-03 | 2026-12-06 | 14-6
| Southern Pine | SS | 2026-08-01 | 2026-12-09 | 16-10 | 21-6 | Note b | 2026-08-01 | 2026-12-09 | 16-10 | 21-6 | Note b
| Southern Pine | #1‡ | 2026-07-10 | 2026-12-03 | 16-2 | 19-3 | 22-10 | 2026-07-10 | 2026-11-07 | 14-9 | 17-3 | 20-5
| Southern Pine | #2‡ | 2026-07-06 | 2026-11-02 | 14-2 | 16-10 | 19-10 | 2026-06-08 | 2000-10-01 | 2026-12-08 | 15-1 | 17-9
| Southern Pine | #3‡ | 2026-05-09 | 2026-08-06 | 2026-10-08 | 13-0 | 15-4 | 2026-05-02 | 2026-07-07 | 2026-09-07 | 2026-11-07 | 13-9
| Spruce-Pine-Fir | SS | 2026-07-08 | 2000-12-01 | 15-10 | 20-2 | 24-7 | 2026-07-08 | 2000-12-01 | 15-10 | 19-9 | 22-10
| Spruce-Pine-Fir | #1 | 2026-07-06 | 2026-11-09 | 15-1 | 18-5 | 21-5 | 2026-07-03 | 2026-10-08 | 13-6 | 16-6 | 19-2
| Spruce-Pine-Fir | #2 | 2026-07-06 | 2026-11-09 | 15-1 | 18-5 | 21-5 | 2026-07-03 | 2026-10-08 | 13-6 | 16-6 | 19-2
| Spruce-Pine-Fir | #3 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2 | 2026-05-06 | 2026-08-01 | 2026-10-03 | 2026-12-06 | 14-6
19.2 | Douglas Fir-Larch | SS | 2026-07-09 | 2026-12-03 | 16-1 | 20-7 | 25-0 | 2026-07-09 | 2026-12-03 | 15-10 | 19-5 | 22-6
| Douglas Fir-Larch | #1 | 2026-07-06 | 2026-11-08 | 14-9 | 18-0 | 20-11 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Douglas Fir-Larch | #2 | 2026-07-04 | 2026-10-11 | 13-9 | 16-10 | 19-6 | 2026-06-08 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6
| Douglas Fir-Larch | #3 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
| Hem-Fir | SS | 2026-07-04 | 2026-11-07 | 15-3 | 19-5 | 23-7 | 2026-07-04 | 2026-11-07 | 15-3 | 19-1 | 22-1
| Hem-Fir | #1 | 2026-07-02 | 2026-11-04 | 14-4 | 17-7 | 20-4 | 2026-06-11 | 2026-10-02 | 2026-12-10 | 15-8 | 18-2
| Hem-Fir | #2 | 2026-06-10 | 2026-10-09 | 13-7 | 16-7 | 19-3 | 2026-06-07 | 2026-09-07 | 2026-12-02 | 14-10 | 17-3
| Hem-Fir | #3 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
| Southern Pine | SS | 2026-07-08 | 2000-12-01 | 15-10 | 20-2 | 24-7 | 2026-07-08 | 2000-12-01 | 15-10 | 20-2 | 24-7
| Southern Pine | #1‡ | 2026-07-04 | 2026-11-07 | 15-1 | 17-7 | 20-11 | 2026-07-01 | 2026-10-07 | 13-5 | 15-9 | 18-8
| Southern Pine | #2‡ | 2026-06-10 | 2026-10-02 | 2026-12-11 | 15-4 | 18-1 | 2026-06-01 | 2026-09-02 | 2026-11-07 | 13-9 | 16-2
| Southern Pine | #3‡ | 2026-05-03 | 2026-07-09 | 2026-09-09 | 2026-11-10 | 14-0 | 2026-04-08 | 2026-06-11 | 2026-08-09 | 2026-10-07 | 2026-12-06
| Spruce-Pine-Fir | SS | 2026-07-02 | 2026-11-04 | 14-11 | 19-0 | 23-1 | 2026-07-02 | 2026-11-04 | 14-9 | 18-0 | 20-11
| Spruce-Pine-Fir | #1 | 2000-07-01 | 2026-10-11 | 13-9 | 16-10 | 19-6 | 2026-06-08 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6
| Spruce-Pine-Fir | #2 | 2000-07-01 | 2026-10-11 | 13-9 | 16-10 | 19-6 | 2026-06-08 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6
| Spruce-Pine-Fir | #3 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
24 | Douglas Fir-Larch | SS | 2026-07-03 | 2026-11-04 | 15-0 | 19-1 | 22-6 | 2026-07-03 | 2026-11-03 | 14-2 | 17-4 | 20-1
| Douglas Fir-Larch | #1 | 2000-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8 | 2026-06-04 | 2026-09-04 | 2026-11-09 | 14-5 | 16-8
| Douglas Fir-Larch | #2 | 2026-06-08 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-05-11 | 2026-08-08 | 2000-11-01 | 13-5 | 15-7
| Douglas Fir-Larch | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-06 | 2026-06-07 | 2026-08-04 | 2026-10-02 | 2026-11-10
| Hem-Fir | SS | 2026-06-10 | 2026-10-09 | 14-2 | 18-0 | 21-11 | 2026-06-10 | 2026-10-09 | 13-11 | 17-0 | 19-9
| Hem-Fir | #1 | 2026-06-08 | 2026-10-02 | 2026-12-10 | 15-8 | 18-2 | 2026-06-02 | 2026-09-01 | 2026-11-06 | 14-0 | 16-3
| Hem-Fir | #2 | 2026-06-04 | 2026-09-07 | 2026-12-02 | 14-10 | 17-3 | 2026-05-10 | 2026-08-07 | 2026-10-10 | 13-3 | 15-5
| Hem-Fir | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-06 | 2026-06-07 | 2026-08-04 | 2026-10-02 | 2026-11-10
| Southern Pine | SS | 2026-07-01 | 2026-11-02 | 14-8 | 18-9 | 22-10 | 2026-07-01 | 2026-11-02 | 14-8 | 18-9 | 22-10
| Southern Pine | #1‡ | 2026-06-10 | 2026-10-07 | 13-5 | 15-9 | 18-8 | 2026-06-04 | 2026-09-06 | 2000-12-01 | 14-1 | 16-8
| Southern Pine | #2‡ | 2026-06-01 | 2026-09-02 | 2026-11-07 | 13-9 | 16-2 | 2026-05-05 | 2026-08-02 | 2026-10-04 | 2026-12-03 | 14-6
| Southern Pine | #3‡ | 2026-04-08 | 2026-06-11 | 2026-08-09 | 2026-10-07 | 2026-12-06 | 2026-04-02 | 2026-06-02 | 2026-07-10 | 2026-09-06 | 2026-11-02
| Spruce-Pine-Fir | SS | 2026-06-08 | 2026-10-06 | 13-10 | 17-8 | 20-11 | 2026-06-08 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Spruce-Pine-Fir | #1 | 2026-06-06 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-05-11 | 2026-08-08 | 2000-11-01 | 13-6 | 15-7
| Spruce-Pine-Fir | #2 | 2026-06-06 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-05-11 | 2026-08-08 | 2000-11-01 | 13-6 | 15-7
| Spruce-Pine-Fir | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-06 | 2026-06-07 | 2026-08-04 | 2026-10-02 | 2026-11-10

## 2308.7.2(6)
TABLE 2308.7.2(6)
RAFTER SPANS FOR COMMON LUMBER SPECIES
(Ground snow load = 50 psf, Ceiling Attached to Rafters, L/Δ = 240)
|  |  | DEAD LOAD = 10 psf |  |  |  |  | DEAD LOAD = 20 psf
RAFTER SPACING (inches) | SPECIES AND GRADE |  | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12 | 2 × 4 | 2 × 6 | 2 × 8 | 2 × 10 | 2 × 12
Maximum rafter spansᵃ
|  |  | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.) | (ft. – in.)
12 | Douglas Fir-Larch | SS | 2026-07-08 | 2026-12-01 | 15-11 | 20-3 | 24-8 | 2026-07-08 | 2026-12-01 | 15-11 | 20-3 | 24-0
| Douglas Fir-Larch | #1 | 2026-07-05 | 2026-11-07 | 15-3 | 18-7 | 21-7 | 2026-07-05 | 2026-11-02 | 14-0 | 17-3 | 20-0
| Douglas Fir-Larch | #2 | 2026-07-03 | 2026-11-03 | 14-3 | 17-5 | 20-2 | 2026-07-01 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Douglas Fir-Larch | #3 | 2026-05-10 | 2026-08-06 | 2026-10-09 | 13-2 | 15-3 | 2026-05-05 | 2026-07-10 | 2000-10-01 | 2026-12-02 | 14-1
| Hem-Fir | SS | 2026-07-03 | 2026-11-05 | 15-0 | 19-2 | 23-4 | 2026-07-03 | 2026-11-08 | 15-0 | 19-2 | 23-4
| Hem-Fir | #1 | 2026-07-01 | 2026-11-02 | 14-8 | 18-1 | 21-0 | 2026-07-01 | 2026-10-10 | 13-9 | 16-9 | 19-5
| Hem-Fir | #2 | 2026-06-09 | 2026-10-08 | 14-0 | 17-2 | 19-11 | 2026-06-09 | 2026-10-03 | 13-0 | 15-10 | 18-5
| Hem-Fir | #3 | 2026-05-10 | 2026-08-06 | 2026-10-09 | 13-2 | 15-3 | 2026-05-05 | 2026-07-10 | 2000-10-01 | 2026-12-02 | 14-1
| Southern Pine | SS | 2026-07-06 | 2026-11-10 | 15-7 | 19-11 | 24-3 | 2026-07-06 | 2026-11-10 | 15-7 | 19-11 | 24-3
| Southern Pine | #1‡ | 2026-07-03 | 2026-11-05 | 15-0 | 18-2 | 21-7 | 2026-07-03 | 2026-11-04 | 14-5 | 16-10 | 20-0
| Southern Pine | #2‡ | 2026-06-11 | 2026-10-06 | 13-4 | 15-10 | 18-8 | 2026-06-06 | 2026-09-09 | 2026-12-04 | 14-8 | 17-3
| Southern Pine | #3‡ | 2026-05-05 | 2000-08-01 | 2026-10-01 | 2026-12-03 | 14-6 | 2000-05-01 | 2026-07-05 | 2026-09-04 | 2026-11-04 | 13-5
| Spruce-Pine-Fir | SS | 2026-07-01 | 2026-11-02 | 14-8 | 18-9 | 22-10 | 2026-07-01 | 2026-11-02 | 14-8 | 18-9 | 22-4
| Spruce-Pine-Fir | #1 | 2026-06-11 | 2026-10-11 | 14-3 | 17-5 | 20-2 | 2026-06-11 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Spruce-Pine-Fir | #2 | 2026-06-11 | 2026-10-11 | 14-3 | 17-5 | 20-2 | 2026-06-11 | 2026-10-05 | 13-2 | 16-1 | 18-8
| Spruce-Pine-Fir | #3 | 2026-05-10 | 2026-08-06 | 2026-10-09 | 13-2 | 15-3 | 2026-05-05 | 2026-07-10 | 2000-10-01 | 2026-12-02 | 14-1
16 | Douglas Fir-Larch | SS | 2000-07-01 | 2000-11-01 | 14-5 | 18-5 | 22-5 | 2000-07-01 | 2000-11-01 | 14-5 | 17-11 | 20-10
| Douglas Fir-Larch | #1 | 2026-06-09 | 2026-10-05 | 13-2 | 16-1 | 18-8 | 2026-06-07 | 2026-09-08 | 2026-12-02 | 14-11 | 17-3
| Douglas Fir-Larch | #2 | 2026-06-07 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2
| Douglas Fir-Larch | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-08 | 2026-06-10 | 2026-08-08 | 2026-10-06 | 2026-12-03
| Hem-Fir | SS | 2026-06-07 | 2026-10-04 | 13-8 | 17-5 | 21-2 | 2026-06-07 | 2026-10-04 | 13-8 | 17-5 | 20-5
| Hem-Fir | #1 | 2026-06-05 | 2026-10-02 | 2026-12-10 | 15-8 | 18-2 | 2026-06-05 | 2026-09-05 | 2026-11-11 | 14-6 | 16-10
| Hem-Fir | #2 | 2026-06-02 | 2026-09-07 | 2026-12-02 | 14-10 | 17-3 | 2026-06-01 | 2026-08-11 | 2026-11-03 | 13-9 | 15-11
| Hem-Fir | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-08 | 2026-06-10 | 2026-08-08 | 2026-10-06 | 2026-12-03
| Southern Pine | SS | 2026-06-10 | 2026-10-09 | 14-2 | 18-1 | 22-0 | 2026-06-10 | 2026-10-09 | 14-2 | 18-1 | 21-10‡
| Southern Pine | #1‡ | 2026-06-07 | 2026-10-04 | 13-5 | 15-9 | 18-8 | 2026-06-07 | 2026-09-10 | 2026-12-05 | 14-7 | 17-3
| Southern Pine | #2‡ | 2026-06-01 | 2026-09-02 | 2026-11-07 | 13-9 | 16-2 | 2026-05-08 | 2026-08-05 | 2026-10-09 | 2026-12-09 | 15-0
| Southern Pine | #3‡ | 2026-04-08 | 2026-06-11 | 2026-08-09 | 2026-10-07 | 2026-12-06 | 2026-04-04 | 2026-06-05 | 2026-08-01 | 2026-09-10 | 2026-11-07
| Spruce-Pine-Fir | SS | 2026-06-05 | 2026-10-02 | 13-4 | 17-0 | 20-9 | 2026-06-05 | 2026-10-02 | 13-4 | 16-8 | 19-4
| Spruce-Pine-Fir | #1 | 2026-06-04 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2
| Spruce-Pine-Fir | #2 | 2026-06-04 | 2026-09-09 | 2026-12-04 | 15-1 | 17-6 | 2026-06-02 | 2000-09-01 | 2026-11-05 | 13-11 | 16-2
| Spruce-Pine-Fir | #3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2 | 2026-04-08 | 2026-06-10 | 2026-08-08 | 2026-10-06 | 2026-12-03
19.2 | Douglas Fir-Larch | SS | 2026-06-07 | 2026-10-04 | 13-7 | 17-4 | 20-6 | 2026-06-07 | 2026-10-04 | 13-5 | 16-5 | 19-0
| Douglas Fir-Larch | #1 | 2026-06-04 | 2026-09-06 | 2000-12-01 | 14-8 | 17-1 | 2000-06-01 | 2026-08-10 | 2026-11-02 | 13-7 | 15-9
| Douglas Fir-Larch | #2 | 2026-06-01 | 2026-08-11 | 2026-11-03 | 13-9 | 15-11 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9
| Douglas Fir-Larch | #3 | 2026-04-07 | 2026-06-09 | 2026-08-06 | 2026-10-05 | 2026-12-01 | 2026-04-03 | 2026-06-03 | 2026-07-11 | 2026-09-07 | 2026-11-02
| Hem-Fir | SS | 2026-06-02 | 2026-09-09 | 2026-12-10 | 16-5 | 19-11 | 2026-06-02 | 2026-09-09 | 2026-12-10 | 16-1 | 18-8
| Hem-Fir | #1 | 2026-06-01 | 2026-09-03 | 2026-11-09 | 14-4 | 16-7 | 2026-05-10 | 2026-08-07 | 2026-10-10 | 13-3 | 15-5
| Hem-Fir | #2 | 2026-05-09 | 2026-08-09 | 2026-11-01 | 13-7 | 15-9 | 2026-05-07 | 2026-08-01 | 2026-10-03 | 2026-12-07 | 14-7
| Hem-Fir | #3 | 2026-04-07 | 2026-06-09 | 2026-08-06 | 2026-10-05 | 2026-12-01 | 2026-04-03 | 2026-06-03 | 2026-07-11 | 2026-09-07 | 2026-11-02
| Southern Pine | SS | 2026-06-05 | 2026-10-02 | 13-4 | 17-0 | 20-9 | 2026-06-05 | 2026-10-02 | 13-4 | 16-11 | 20-0
| Southern Pine | #1 | 2026-06-02 | 2026-09-08 | 2026-12-03 | 14-4 | 17-1 | 2000-06-01 | 2000-09-01 | 2026-11-04 | 13-4 | 15-9
| Southern Pine | #2 | 2026-05-07 | 2026-08-04 | 2026-10-07 | 2026-12-06 | 14-9 | 2026-05-02 | 2026-07-09 | 2026-09-09 | 2026-11-07 | 13-8
| Southern Pine | #3 | 2026-04-03 | 2026-06-04 | 2000-08-01 | 2026-09-08 | 2026-11-05 | 2000-04-01 | 2026-05-10 | 2026-07-04 | 2026-08-11 | 2026-10-07
| Spruce-Pine-Fir | SS | 2026-06-01 | 2026-09-06 | 2026-12-07 | 16-0 | 19-1 | 2026-06-01 | 2026-09-06 | 2026-12-05 | 15-3 | 17-8
| Spruce-Pine-Fir | #1 | 2026-05-11 | 2026-08-11 | 2026-11-03 | 13-9 | 15-11 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9
| Spruce-Pine-Fir | #2 | 2026-05-11 | 2026-08-11 | 2026-11-03 | 13-9 | 15-11 | 2026-05-07 | 2026-08-03 | 2026-10-05 | 2026-12-09 | 14-9
| Spruce-Pine-Fir | #3 | 2026-04-07 | 2026-06-09 | 2026-08-06 | 2026-10-05 | 2026-12-01 | 2026-04-03 | 2026-06-03 | 2026-07-11 | 2026-09-07 | 2026-11-02
24 | Douglas Fir-Larch | SS | 2026-06-01 | 2026-09-07 | 2026-12-07 | 15-10 | 18-4 | 2026-06-01 | 2026-09-06 | 2000-12-01 | 14-8 | 17-0
| Douglas Fir-Larch | #1 | 2026-05-10 | 2026-08-06 | 2026-10-09 | 13-2 | 15-3 | 2026-05-05 | 2026-07-10 | 2000-10-01 | 2026-12-02 | 14-1
| Douglas Fir-Larch | #2 | 2026-05-05 | 2026-07-11 | 2026-10-01 | 2026-12-04 | 14-3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
| Douglas Fir-Larch | #3 | 2026-04-01 | 2000-06-01 | 2026-07-07 | 2026-09-04 | 2026-10-09 | 2026-03-10 | 2026-05-07 | 2026-07-01 | 2026-08-07 | 2000-10-01
| Hem-Fir | SS | 2026-05-09 | 2026-09-01 | 2026-11-11 | 15-2 | 18-0 | 2026-05-09 | 2026-09-01 | 2026-11-09 | 14-5 | 15-11
| Hem-Fir | #1 | 2026-05-08 | 2026-08-03 | 2026-10-06 | 2026-12-10 | 14-10 | 2026-05-03 | 2026-07-08 | 2026-09-09 | 2026-11-10 | 13-9
| Hem-Fir | #2 | 2026-05-04 | 2026-07-10 | 2026-09-11 | 2026-12-01 | 14-1 | 2026-04-11 | 2026-07-03 | 2026-09-02 | 2026-11-03 | 13-0
| Hem-Fir | #3 | 2026-04-01 | 2000-06-01 | 2026-07-07 | 2026-09-04 | 2026-10-09 | 2026-03-10 | 2026-05-07 | 2026-07-01 | 2026-08-07 | 2000-10-01
| Southern Pine | SS | 2000-06-01 | 2026-09-05 | 2026-12-05 | 15-10 | 19-3 | 2000-06-01 | 2026-09-05 | 2026-12-05 | 15-2‡ | 17-10‡
| Southern Pine | #1‡ | 2026-05-10 | 2026-08-08 | 2000-11-01 | 2026-12-10 | 15-3 | 2026-05-05 | 2000-08-01 | 2026-10-02 | 2026-11-11 | 14-1
| Southern Pine | #2‡ | 2000-05-01 | 2026-07-05 | 2026-09-05 | 2026-11-03 | 13-2 | 2026-04-07 | 2026-06-11 | 2026-08-09 | 2026-10-05 | 2026-12-03
| Southern Pine | #3‡ | 2026-03-10 | 2026-05-08 | 2026-07-01 | 2026-08-08 | 2026-10-03 | 2026-03-06 | 2026-05-03 | 2026-06-07 | 2000-08-01 | 2026-09-06
| Spruce-Pine-Fir | SS | 2026-05-08 | 2026-08-10 | 2026-11-08 | 14-8 | 17-1 | 2026-05-08 | 2026-08-10 | 2026-11-02 | 13-7 | 15-9
| Spruce-Pine-Fir | #1 | 2026-05-05 | 2026-07-11 | 2026-10-01 | 2026-12-04 | 14-3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
| Spruce-Pine-Fir | #2 | 2026-05-05 | 2026-07-11 | 2026-10-01 | 2026-12-04 | 14-3 | 2000-05-01 | 2026-07-04 | 2026-09-04 | 2026-11-05 | 13-2
| Spruce-Pine-Fir | #3 | 2026-04-01 | 2000-06-01 | 2026-07-07 | 2026-09-04 | 2026-10-09 | 2026-03-10 | 2026-05-07 | 2026-07-01 | 2026-08-07 | 2000-10-01

## 2308.7.3.1
TABLE 2308.7.3.1
RAFTER TIE CONNECTIONSᵍ
|  | NO SNOW LOAD |  |  |  | GROUND SNOW LOAD (pounds per square foot)
[6 empty] | 30 pounds per square foot |  |  |  | 50 pounds per square foot
RAFTER SLOPE | TIE SPACING (inches)
|  | 12 | 20 | 28 | 36 | 12 | 20 | 28 | 36 | 12 | 20 | 28 | 36
Required number of 16d common (3½" x 0.162") nailsᵃ⁻ ᵇ per connectionᶜ⁻ ᵈ⁻ ᵉ⁻ ᶠ
3:12 | 12 | 4 | 6 | 8 | 10 | 4 | 6 | 8 | 11 | 5 | 8 | 12 | 15
| 16 | 5 | 7 | 10 | 13 | 5 | 8 | 11 | 14 | 6 | 11 | 15 | 20
| 24 | 7 | 11 | 15 | 19 | 7 | 11 | 16 | 21 | 9 | 16 | 23 | 30
| 32 | 10 | 14 | 19 | 25 | 10 | 16 | 22 | 28 | 12 | 27 | 30 | 40
| 48 | 14 | 21 | 29 | 37 | 14 | 32 | 36 | 42 | 18 | 32 | 46 | 60
4:12 | 12 | 3 | 4 | 5 | 6 | 3 | 5 | 6 | 8 | 4 | 6 | 9 | 11
| 16 | 3 | 5 | 7 | 8 | 4 | 6 | 8 | 11 | 5 | 8 | 12 | 15
| 24 | 4 | 7 | 10 | 12 | 5 | 9 | 12 | 16 | 7 | 12 | 17 | 22
| 32 | 6 | 9 | 13 | 16 | 8 | 12 | 16 | 22 | 10 | 16 | 24 | 30
| 48 | 8 | 14 | 19 | 24 | 10 | 18 | 24 | 32 | 14 | 24 | 34 | 44
5:12 | 12 | 3 | 3 | 4 | 5 | 3 | 4 | 5 | 7 | 3 | 5 | 7 | 9
| 16 | 3 | 4 | 5 | 7 | 3 | 5 | 7 | 9 | 4 | 7 | 9 | 12
| 24 | 4 | 6 | 8 | 10 | 4 | 7 | 10 | 13 | 6 | 10 | 14 | 18
| 32 | 5 | 8 | 10 | 13 | 6 | 10 | 14 | 18 | 8 | 14 | 18 | 24
| 48 | 7 | 11 | 15 | 20 | 8 | 14 | 20 | 26 | 12 | 20 | 28 | 36
7:12 | 12 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 5 | 3 | 4 | 5 | 7
| 16 | 3 | 3 | 4 | 5 | 3 | 4 | 5 | 6 | 3 | 5 | 7 | 9
| 24 | 3 | 4 | 6 | 7 | 3 | 5 | 7 | 9 | 4 | 7 | 10 | 13
| 32 | 4 | 6 | 8 | 10 | 4 | 8 | 10 | 12 | 6 | 10 | 14 | 18
| 48 | 5 | 8 | 11 | 14 | 6 | 10 | 14 | 18 | 9 | 14 | 20 | 26
9:12 | 12 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 5
| 16 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 5 | 3 | 4 | 5 | 7
| 24 | 3 | 3 | 5 | 6 | 3 | 4 | 6 | 7 | 3 | 6 | 8 | 10
| 32 | 3 | 4 | 6 | 8 | 4 | 6 | 8 | 10 | 5 | 8 | 10 | 14
| 48 | 4 | 6 | 9 | 11 | 5 | 8 | 12 | 14 | 7 | 12 | 16 | 20
12:12 | 12 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4
| 16 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 5
| 24 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 6 | 3 | 4 | 6 | 8
| 32 | 3 | 3 | 4 | 5 | 3 | 5 | 6 | 8 | 4 | 6 | 8 | 10
| 48 | 3 | 4 | 6 | 7 | 4 | 7 | 8 | 12 | 6 | 8 | 12 | 16

## 2308.7.5
TABLE 2308.7.5
REQUIRED RATING OF APPROVED UPLIFT CONNECTORS (pounds)ᵃ⁻ ᵇ⁻ ᶜ⁻ ᵉ⁻ ᶠ⁻ ᵍ⁻ ʰ
OVERHANGS (pounds/feet)ᵈ | ROOF SPAN (feet) | [6 empty] | OVERHANGS (pounds/feet)ᵈ
| 12 | 20 | 24 | 28 | 32 | 36 | 40
85 | -72 | -120 | -145 | -169 | -193 | -217 | -241 | -38.55
90 | -91 | -151 | -181 | -212 | -242 | -272 | -302 | -43.22
100 | -131 | -281 | -262 | -305 | -349 | -393 | -436 | -53.36
110 | -175 | -292 | -351 | -409 | -467 | -526 | -584 | -64.56

## WIND EXPOSURE FACTOR
Mean Roof Height (feet)
EXPOSURE | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
B | 1 | 1 | 1 | 1 | 1.05 | 1.09 | 1.12 | 1.16 | 1.19 | 1.22
C | 1.21 | 1.29 | 1.35 | 1.4 | 1.45 | 1.49 | 1.53 | 1.56 | 1.59 | 1.62
D | 1.47 | 1.55 | 1.61 | 1.66 | 1.7 | 1.74 | 1.78 | 1.81 | 1.84 | 1.87

## 2308.7.12
TABLE 2308.7.12
SPANa (feet) | LIVE LOAD (pounds per square foot) | DEFLECTION LIMIT | BENDING STRESS (f) (pounds per square inch) | MODULUS OF ELASTICITY (E) (pounds per square inch)
Roofs
4 | 20 | 1/240 | 160 | 170000
|  | 1/360 |  | 256000
| 30 | 1/240 | 210 | 256000
|  | 1/360 |  | 384000
| 40 | 1/240 | 270 | 340000
|  | 1/360 |  | 512000
4.5 | 20 | 1/240 | 200 | 242000
|  | 1/360 |  | 305000
| 30 | 1/240 | 270 | 363000
|  | 1/360 |  | 405000
| 40 | 1/240 | 350 | 484000
|  | 1/360 |  | 725000
5 | 20 | 1/240 | 250 | 332000
|  | 1/360 |  | 500000
| 30 | 1/240 | 330 | 495000
|  | 1/360 |  | 742000
| 40 | 1/240 | 420 | 660000
|  | 1/360 |  | 1000000
5.5 | 20 | 1/240 | 300 | 442000
|  | 1/360 |  | 660000
| 30 | 1/240 | 400 | 662000
|  | 1/360 |  | 998000
| 40 | 1/240 | 500 | 884000
|  | 1/360 |  | 1330000
6 | 20 | 1/240 | 360 | 575000
|  | 1/360 |  | 862000
| 30 | 1/240 | 480 | 862000
|  | 1/360 |  | 1295000
| 40 | 1/240 | 600 | 1150000
|  | 1/360 |  | 1730000
6.5 | 20 | 1/240 | 420 | 595000
|  | 1/360 |  | 892000
| 30 | 1/240 | 560 | 892000
|  | 1/360 |  | 1340000
| 40 | 1/240 | 700 | 1190000
|  | 1/360 |  | 1730000
7 | 20 | 1/240 | 490 | 910000
|  | 1/360 |  | 1360000
| 30 | 1/240 | 650 | 1370000
|  | 1/360 |  | 2000000
| 40 | 1/240 | 810 | 1820000
|  | 1/360 |  | 2725000
7.5 | 20 | 1/240 | 560 | 1125000
|  | 1/360 |  | 1685000
| 30 | 1/240 | 750 | 1685000
|  | 1/360 |  | 2530000
| 40 | 1/240 | 930 | 2250000
|  | 1/360 |  | 3380000
8 | 20 | 1/240 | 640 | 1360000
|  | 1/360 |  | 2040000
| 30 | 1/240 | 850 | 2040000
|  | 1/360 |  | 3060000
Floors
4 | 40 | 1/360 | 840 | 1000000
4.5 | 40 | 1/360 | 950 | 1300000
5 | 40 | 1/360 | 1060 | 1600000

## 2406.2(1)
TABLE 2406.2(1)
MINIMUM CATEGORY CLASSIFICATION OF GLAZING USING CPSC 16 CFR 1201
EXPOSED SURFACE AREA OF ONE SIDE OF ONE LITE | GLAZING IN STORM OR COMBINATION DOORS (Category class) | GLAZING IN DOORS (Category class) | GLAZED PANELS REGULATED BY SECTION 2406.4.3 (Category class) | GLAZED PANELS REGULATED BY SECTION 2406.4.2 (Category class) | DOORS AND ENCLOSURES REGULATED BY SECTION 2406.4.5 (Category class) | SLIDING GLASS DOORS PATIO TYPE (Category class)
9 square feet or less | I | I | No requirement | I | II | II
More than 9 square feet | II | II | II | II | II | II

## 2406.2(2)
TABLE 2406.2(2)
MINIMUM CATEGORY CLASSIFICATION OF GLAZING USING ANSI Z97.1
EXPOSED SURFACE AREA OF ONE SIDE OF ONE LITE | GLAZED PANELS REGULATED BY SECTION 2406.4.3 (Category class) | GLAZED PANELS REGULATED BY SECTION 2406.4.2 (Category class) | DOORS AND ENCLOSURES REGULATED BY SECTION 2406.4.5a (Category class)
9 square feet or less | No requirement | B | A
More than 9 square feet | A | A | A

## 2506.2
TABLE 2506.2
GYPSUM BOARD AND GYPSUM PANEL PRODUCTS MATERIALS AND ACCESSORIES
MATERIAL | STANDARD
Abuse resistant non-decorated interior gypsum panel products and fiber-reinforced cement panels | ASTM C 1629
Accessories for gypsum board | ASTM C 1047
Adhesives for fastening gypsum wallboard | ASTM C 557
Cold-formed steel studs and track, structural | AISI S200 and ASTM C 955, Section 8
Cold-formed steel studs and track, nonstructural | AISI S220 and ASTM C 645, Section 10
Elastomeric joint sealants | ASTM C 920
Fiber-reinforced gypsum panels | ASTM C 1278
Glass mat gypsum backing panel | ASTM C 1178
Glass mat gypsum panel 5 | ASTM C 1658
Glass mat gypsum substrate | ASTM C 1177
Joint reinforcing tape and compound | ASTM C 474; C 475
Nails for gypsum boards | ASTM C 514, F 547, F 1667
Steel screws | ASTM C 954; C 1002
Standard specification for gypsum board | ASTM C 1396
Testing gypsum and gypsum products | ASTM C 22; C 472; C 473

## 2507.2
TABLE 2507.2
LATH, PLASTERING MATERIALS AND ACCESSORIES
MATERIAL | STANDARD
Accessories for gypsum veneer base | ASTM C 1047
Blended cement | ASTM C 595
Cold-formed steel studs and track, nonstructural | AISI S220 and ASTM C 645, Section 10
Cold-formed steel studs and track, structural | AISI S200 and ASTM C 955, Section 8
Exterior plaster bonding compounds | ASTM C 932
Gypsum casting and molding plaster | ASTM C 59
Gypsum Keene’s cement | ASTM C 61
Gypsum plaster | ASTM C 28
Gypsum veneer plaster | ASTM C 587
Hydraulic cement | ASTM C 1157; C 1600
Interior bonding compounds, gypsum | ASTM C 631
Lime plasters | ASTM C 5; C 206
Masonry cement | ASTM C 91
Metal lath | ASTM C 847
Plaster aggregates Sand Perlite Vermiculite | ASTM C 35; C 897 ASTM C 35 ASTM C 35
Plastic cement | ASTM C 1328
Portland cement | ASTM C 150
Steel screws | ASTM C 1002; C 954
Welded wire lath | ASTM C 933
Woven wire plaster base | ASTM C 1032

## 2508.1
TABLE 2508.1
INSTALLATION OF GYPSUM CONSTRUCTION
MATERIAL | STANDARD
Gypsum board and gypsum panel products | GA-216; ASTM C 840
Gypsum sheathing and gypsum panel products | ASTM C 1280
Gypsum board (Interior) | ASTM C 1396
Gypsum board (Exterior) | ASTM C 1396
Gypsum veneer base | ASTM C 844
Interior lathing and furring | ASTM C 841
Steel framing for gypsum board and gypsum panel products | ASTM C 754; C 1007

## 2508.5
TABLE 2508.5
SHEAR CAPACITY FOR HORIZONTAL WOOD-FRAME GYPSUM BOARD DIAPHRAGM CEILING ASSEMBLIES
MATERIAL | THICKNESS OF MATERIAL (MINIMUM) (inches) | SPACING OF FRAMING MEMBERS (inches) | SHEAR VALUEa, b (PLF OF CEILING) | MINIMUM FASTENER SIZE
Gypsum board or gypsum panel product | 2026-01-02 | 16 o.c. | 90 | 5d cooler or wallboard nail; 1⅝-inch long; 0.086-inch shank; ¹⁵⁄₆₄-inch headc
Gypsum board or gypsum panel product | 2026-01-02 | 24 o.c. | 70 | 5d cooler or wallboard nail; 1⅝-inch long; 0.086-inch shank; ¹⁵⁄₆₄-inch headc

## 2509.2
TABLE 2509.2
BACKERBOARD MATERIALS
MATERIAL | STANDARD
Glass mat water-resistant gypsum backing panel | ASTM C 1178
Discrete nonasbestos fiber cement interior substrate sheets | ASTM C 1288
Nonasbestos fiber cement flat sheets | ISO 8336, Category C
Nonasbestos fiber-mat reinforced cementitious backer unit | ASTM C 1325

## 2511.1
TABLE 2511.1
INSTALLATION OF PLASTER CONSTRUCTION
MATERIAL | STANDARD
Cement plaster | ASTM C 926
Gypsum plaster | ASTM C 842
Gypsum veneer plaster | ASTM C 843
Interior lathing and furring (gypsum plaster) | ASTM C 841
Lathing and furring (cement plaster) | ASTM C 1063
Steel framing | ASTM C 754; C 1007

## 2512.6
TABLE 2512.6
CEMENT PLASTERS
COAT | MINIMUM PERIOD MOIST CURING | MINIMUM INTERVAL BETWEEN COATS
First | 48 hoursa | 48 hoursb
Second | 48 hours | 7 daysc
Finish | — | Note c

## 2603.12.1
TABLE 2603.12.1
CLADDING MINIMUM FASTENING REQUIREMENTS FOR DIRECT ATTACHMENT OVER FOAM PLASTIC SHEATHING TO SUPPORT CLADDING WEIGHTa
MAXIMUM THICKNESS OF FOAM SHEATHINGc (inches)
CLADDING FASTENER THROUGH FOAM SHEATHING INTO: | CLADDING FASTENER TYPE AND MINIMUM SIZEb | CLADDING FASTENER VERTICAL SPACING (inches) | 16" o.c. fastener horizontal spacing |  |  | 24" o.c. fastener horizontal spacing
|  |  | Cladding weight |  |  | Cladding weight
|  |  | 3 psf | 11 psf | 25 psf | 3 psf | 11 psf | 25 psf
Steel framing (minimum penetration of steel thickness plus 3 threads) | #8 screw into 33 mil steel or thicker | 6 | 3 | 3 | 1.5 | 3 | 2 | DR
|  | 8 | 3 | 2 | 0.5 | 3 | 1.5 | DR
|  | 12 | 3 | 1.5 | DR | 3 | 0.75 | DR
| #10 screw into 33 mil steel | 6 | 4 | 3 | 2 | 4 | 3 | 0.5
|  | 8 | 4 | 3 | 1 | 4 | 2 | DR
|  | 12 | 4 | 2 | DR | 3 | 1 | DR
| #10 screw into 43 mil steel or thicker | 6 | 4 | 4 | 3 | 4 | 4 | 2
|  | 8 | 4 | 4 | 2 | 4 | 3 | 1.5
|  | 12 | 4 | 3 | 1.5 | 4 | 3 | DR

## 2603.12.2
TABLE 2603.12.2
FURRING MINIMUM FASTENING REQUIREMENTS FOR APPLICATION OVER FOAM PLASTIC SHEATHING TO SUPPORT CLADDING WEIGHTa
MAXIMUM THICKNESS OF FOAM SHEATHINGd (inches)
FURRING MATERIAL | FRAMING MEMBER | FASTENER TYPE AND MINIMUM SIZEb | MINIMUM PENETRATION INTO WALL FRAMING (inches) | FASTENER SPACING IN FURRING (inches) | 16" o.c. furringc |  |  | 24" o.c. furringc
[5 empty] | Cladding weight |  |  | Cladding weight
[5 empty] | 3 psf | 11 psf | 25 psf | 3 psf | 11 psf | 25 psf
Minimum 33 mil steel furring or minimum 1x wood furringc | 33 mil steel stud | #8 screw | Steel thickness plus 3 threads | 12 | 3 | 1.5 | DR | 3 | 0.5 | DR
|  |  |  | 16 | 3 | 1 | DR | 2 | DR | DR
|  |  |  | 24 | 2 | DR | DR | 2 | DR | DR
|  | #10 screw | Steel thickness plus 3 threads | 12 | 4 | 2 | DR | 4 | 1 | DR
|  |  |  | 16 | 4 | 1.5 | DR | 3 | DR | DR
|  |  |  | 24 | 3 | DR | DR | 2 | DR | DR
| 43 mil or thicker steel stud | #8 Screw | Steel thickness plus 3 threads | 12 | 3 | 1.5 | DR | 3 | 0.5 | DR
|  |  |  | 16 | 3 | 1 | DR | 2 | DR | DR
|  |  |  | 24 | 2 | DR | DR | 2 | DR | DR
|  | #10 screw | Steel thickness plus 3 threads | 12 | 4 | 3 | 1.5 | 4 | 3 | DR
|  |  |  | 16 | 4 | 3 | 0.5 | 4 | 2 | DR
|  |  |  | 24 | 4 | 2 | DR | 4 | 0.5 | DR

## 2607.4
TABLE 2607.4
AREA LIMITATION AND SEPARATION REQUIREMENTS FOR LIGHT-TRANSMITTING PLASTIC WALL PANELSa
MINIMUM SEPARATION OF PLASTIC WALL PANELS (feet)
FIRE SEPARATION DISTANCE (feet) | CLASS OF PLASTIC | MAXIMUM PERCENTAGE AREA OF EXTERIOR WALL IN PLASTIC WALL PANELS | MAXIMUM SINGLE AREA OF PLASTIC WALL PANELS (square feet) | Vertical | Horizontal
Less than 6 | — | Not Permitted | Not Permitted | — | —
6 or more but less than 11 | CC1 | 10 | 50 | 8 | 4
| CC2 | Not Permitted | Not Permitted | — | —
11 or more but less than or equal to 30 | CC1 | 25 | 90 | 6 | 4
| CC2 | 15 | 70 | 8 | 4
Over 30 | CC1 | 50 | Not Limited | 3b | 0
| CC2 | 50 | 100 | 6b | 3

## 2609.4
TABLE 2609.4
AREA LIMITATIONS FOR LIGHT-TRANSMITTING PLASTIC ROOF PANELS
CLASS OF PLASTIC | MAXIMUM AREA OF INDIVIDUAL ROOF PANELS (square feet) | MAXIMUM AGGREGATE AREA OF ROOF PANELS (percent of floor area)
CC1 | 300 | 30
CC2 | 100 | 25

## 3304.4.1
TABLE 3304.4.1
MINIMUM SIZES OF TIMBER BRACING AND TIMBER SHEET PILING FOR TRENCHES
NOT EXCEEDING 10 FEET (3048 MM) IN DEPTH AND 15 FEET (4572 MM) IN WIDTH
DEPTH OF TRENCH | WIDTH OF TRENCH | NOMINAL SIZE OF CROSS BRACING AT 6 FEET (1829 mm) HORIZONTAL SPACING | SHORING
Up to 10 ft (3048 mm) | Up to 9 ft (2743 mm) | 6 in × 8 in (152 mm × 203 mm) | Sheet Piling, 2 in × 6 in (51 mm × 152 mm), spaced tight, and Wales, 12 in x 12 in (305 mm x 305 mm), with 5 ft (1524 mm) maximum vertical spacing
| Up to 15 ft (4572 mm) | 8 in × 8 in (152 mm × 203 mm)

## 3304.4.2
TABLE 3304.4.2
MAXIMUM ALLOWABLE SLOPES AND STEPS
SOIL TYPE | MAXIMUM ALLOWABLE SLOPES (Horizontal:Vertical) | MAXIMUM ALLOWABLE BENCH STEP
Type A soil | 1:1 (45°) | 5 feet (1524 mm)
Type B soil | 1:1 (45°) | 4 feet (1219 mm)
Type C soil | 1½:1 (34°) | Not allowed

## 3305.3.2.3
TABLE 3305.3.2.3
MINIMUM LATERAL PRESSURES TO BE ASSUMED FOR FRESH CONCRETE WEIGHING 150 POUNDS PER FOOTᵃʰ ᶜ
TYPE OF WORK | MINIMUM LATERAL PRESSURE ASSUMED (PSF) | LIMITATIONS
Columns: Ordinary work with normal internal vibration | p = 150 + (9000R/T) | Maximum 3,000 psf or 150h, whichever is less
Walls: Rate of placement at 7 feet per hour or less | p = 150 + (9000R/T) | Maximum 2,000 psf or 150h, whichever is less
Walls: Rate of placement at greater than 7 feet per hour | p = 150 + (43400/T) + (2800R/T) | Maximum 2,000 psf or 150h, whichever is less
Slabs | p = 150h | None

## 3314.4.4.12
TABLE 3314.4.4.12
MINIMUM DISTANCES FROM POWER LINES
INSULATED LINES
Voltage | Minimum distance | Alternatives
Less than 300 volts | 3 feet (914 mm) | Two times the length of the line insulator, but never less than 10 feet (3048 mm).
300 volts to 50 kilovolts | 10 feet (3048 mm) | Two times the length of the line insulator, but never less than 10 feet (3048 mm).
More than 50 kilovolts | 10 feet (3048 mm) plus 0.4 inches (10 mm) for each 1 kilovolt over 50 kilovolts.
UNINSULATED LINES
Voltage | Minimum distance | Alternatives
Less than 50 kilovolts | 10 feet (3.1 m) | Two times the length of the line insulator, but never less than 10 feet (3048 mm).
More than 50 kilovolts | 10 feet (3.1 m) plus 0.4 inches (10 mm) for each 1 kilovolt over 50 kilovolts.

## 3314.5.2
TABLE 3314.5.2
MAXIMUM PERMISSIBLE SPANS FOR 2-INCH PLANK USED ON SCAFFOLDS
| FULL THICKNESS UNDRESSED LUMBER |  |  | LUMBER OF NOMINAL THICKNESS
MATERIAL | 25 | 50 | 75 | 25 | 50 | 75
Working Load (psf) | 25 | 50 | 75 | 25 | 50 | 75
Permissible Span (ft) | 10 | 8 | 6 | 8 | 6 | 5

## 3314.12.1(1)
TABLE 3314.12.1(1)
MINIMUM SIZE AND MAXIMUM SPACING OF MEMBERS OF SINGLE WOOD POLE LIGHT DUTY SCAFFOLDS
UNIFORMLY DISTRIBUTED LOAD NOT TO EXCEED 25 psf
Max. height of scaffold (ft) | 20' | 40' | 60' | 75'
|  |  |  | Top 60' | Lower Sect.
Poles or uprights (minimum) | 2" × 4" | 3" × 4" | 4" × 4" | 4" × 4" | 4" × 6"
Pole foundation (minimum) | 2" × 9"
Max. pole spacing (longitudinal) | 10'-0"
Max. width of scaffold | 5'-0"
Bearers or putlogs (minimum) | 3" × 4" or 2" × 6" (on edge)
Ledgers (minimum)
With 6'-0" pole space | 1" × 6" (on edge)
With 10'-0" pole space | 1¼" × 9" (on edge)
Vertical spacing of ledgers (maximum) | 7'-0"
Nonsupporting stringers | 1" × 4"
Tie-ins | 1" × 4"
Bracing | 1" × 4"
Planking
Not more than 6' span | 1¼" × 9"
Up to 10' span | 2" × 9"
Toeboards | 1" × 6"
Guardrails | 2" × 4"

## 3314.12.1(2)
TABLE 3314.12.1(2)
MINIMUM SIZE AND MAXIMUM SPACING OF MEMBERS OF SINGLE WOOD POLE MEDIUM DUTY SCAFFOLDS
UNIFORMLY DISTRIBUTED LOAD NOT TO EXCEED 50 psf
Max. height of scaffold | 20' | 40' | 60' | 75'
|  |  |  | Top 60' | Lower Sect.
Poles or uprights (minimum) | 3" × 4" or 2" × 6" | 4" × 4" | 4" × 6" | 4" × 4" | 4" × 6"
Pole foundation (minimum) | 2"×9"
Max. pole spacing (longitudinal) | 8'-0"
Max. width of scaffold | 5'-0" |  | 8'-0"
Bearers or putlogs (minimum) | 3" × 4" or 2" × 6" (on edge) |  | 3" × 5" or 2" × 9" (on edge)
Max. spacing of bearers or putlogs | 8'-0"
Ledgers (minimum) | 2" × 9" (on edge)
Vertical spacing of ledgers (maximum) | 7" × 0"
Nonsupporting stringers | 1"×6" or 1¼" × 4"
Tie-ins | 1" × 6"
Bracing | 1" × 6"
Planking
Not more than 6' span | 1¼" × 9"
Up to 8' span | 2" × 9"
Toeboards | 2" × 9"
Guardrails | 2" × 4"

## 3314.12.1(3)
TABLE 3314.12.1(3)
MINIMUM SIZE AND MAXIMUM SPACING OF MEMBERS OF SINGLE WOOD POLE HEAVY DUTY SCAFFOLDS
UNIFORMLY DISTRIBUTED LOAD NOT TO EXCEED 75 psf
Max. height of scaffold | 20' | 40' | 60' | 75'
|  |  |  | Top 60' | Lower Sect.
Poles or uprights (minimum) | 3" × 4" or 2" × 6" | 4" × 4" | 4" × 6" | 4" × 6" | 6" × 6"
Pole foundation (minimum) | 2" × 9"
Max. pole spacing (longitudinal) | 6'-0"
Max. width of scaffold | 5'-0" |  | 8'-0"
Bearers or putlogs (minimum) | 3" × 5" |  | 3" × 6" or 2" × 9"
Max. spacing of bearers or putlogs | 6'-0"
Ledgers (minimum) | 2" × 9" (on edge)
Vertical spacing of ledgers (maximum) | 7" × 0"
Nonsupporting stringers | 2" × 4"
Tie-ins | 1" × 6"
Bracing | 1" × 6"
Planking | 2" × 9"
Toeboards | 2" × 9"
Guardrails | 2" × 4"

## 3314.12.1(4)
TABLE 3314.12.1(4)
MINIMUM SIZE AND MAXIMUM SPACING OF MEMBERS OF INDEPENDENT WOOD POLE LIGHT DUTY SCAFFOLDS
UNIFORMLY DISTRIBUTED LOAD NOT TO EXCEED 25 psf
Max. height of scaffold (ft) | 20' | 40' | 60' | 75'
|  |  |  | Top 60' | Lower Sect.
Poles or uprights (minimum) | 2" × 4" | 3" × 4" or 2" × 6" | 4" × 4" | 4" × 4" | 4" × 6"
Pole foundation (minimum) | 2" × 9"
Max. pole spacing (longitudinal)
With 1 ¼" × 9" ledgers | 6'-0"
With 2" × 9" ledgers | 10'-0"
Max. pole spacing (transverse) | 10'-0"ᵃ
Ledgers (minimum) | 1¼" × 9" (on edge) or 2" × 9"
Vertical spacing of ledgers (maximum) | 7'-0"
Bearers (minimum) | 1¼" × 9" (on edge)
Nonsupporting stringers | 1" × 4"
Bracing | 1" × 4"
Planking
Not more than 6' span | 1¼" × 9"
Up to 8' span | 2" × 9"
Toeboards | 1" × 6"
Guardrails | 2" × 4"

## 3314.12.1(5)
TABLE 3314.12.1(5)
MINIMUM SIZE AND MAXIMUM SPACING OF MEMBERS OF INDEPENDENT WOOD POLE MEDIUM DUTY SCAFFOLDS
UNIFORMLY DISTRIBUTED LOAD NOT TO EXCEED 50 psf
Max. height of scaffold (ft) | 20' | 40' | 60' | 75'
|  |  |  | Top 60' | Lower Sect.
Poles or uprights (minimum) | 3" × 4" or 2" × 6" | 4" × 4" | 4" × 6" | 4" × 6" | 6" × 6"
Pole foundation (minimum) | 2" × 9"
Max. pole spacing (longitudinal) | 8'-0"
Max. pole spacing (transverse) | 10'-0"ᵃ
Ledgers (minimum) | 2" × 9" (on edge)
Vertical spacing of ledgers (maximum) | 6'-0"
Bearers (minimum) | 2" × 9" (on edge)
Nonsupporting stringers | 1¼" × 4" or 1" × 6"
Bracing | 1" × 6"
Planking
Not more than 6' span | 1¼" × 9"
Up to 6' span | 2" × 9"
Toeboards | 2" × 9"
Guardrails | 2" × 4"

## 3314.12.1(6)
TABLE 3314.12.1(6)
MINIMUM SIZE AND MAXIMUM SPACING OF MEMBERS OF INDEPENDENT WOOD POLE HEAVY DUTY SCAFFOLDS
UNIFORMLY DISTRIBUTED LOAD NOT TO EXCEED 75 psf
Max. height of scaffold (ft) | 20' | 40' | 60' | 75'
|  |  |  | Top 60' | Lower Sect.
Poles or uprights (minimum) | 4" × 4" | 4" × 4" | 4" × 6" | 4" × 6" | 6" × 6"
Pole foundation (minimum) | 2" × 9"
Max. pole spacing (longitudinal) | 6'-0"ᵃ
Max. pole spacing (transverse) | 10'-0"ᵃ
Ledgers (minimum) | 2" × 9" (on edge)
Vertical spacing of ledgers (maximum) | 5'-0"
Bearers (minimum) | 2" x 9" (on edge)
Nonsupporting stringers | 1¼" × 9"
Bracing | 1" × 6"
Planking | 2" × 9"
Toeboards | 2" × 9"
Guardrails | 2" × 4"

## 3314.12.3
TABLE 3314.12.3
SIZE AND NUMBER OF NAILS REQUIRED FOR SCAFFOLD CONSTRUCTION
THICKNESS OF SMALLER MEMBER (inch) | TRADE SIZE OF NAIL | LENGTH OF NAIL (inch)
1 | 8d | 2½
2 | 20d | 4
3 | 60d | 6
4 | — | 8
Width of Smaller Member (inch) |  | Minimum Number of Nails Required
4 |  | 2
6 |  | 3
8 |  | 4
10 |  | 5
12 |  | 5

## 3319.13
TABLE 3319.13
WIND MEASUREMENT REQUIREMENTS FOR CRANES AND DERRICKS
EQUIPMENT TYPE |  | ALLOWABLE OPTIONS
|  | Option 1: Anemometer on the crane or derrick | Option 2: Anemometer at the site | Option 3: Nearest weather station
Certificate of on-site inspection or supervision by a licensed master rigger required | Crane with lattice boom, jib, or mast (and not a pile driver or clamshell) | Yes | No (Except may utilize if anemometer on crane malfunctions) | No
| Crane utilizing only a telescoping boom | Yes | Yes | Yes
| Crane utilizing only an articulating boom | Yes | Yes | Yes
| Pile driver | Yes | Yes | Yes
| Clamshell | Yes | Yes | Yes
| Derrick | Yes | Yes | No
A crane, derrick, pile driver, or clamshell that does not require a certificate of on-site inspection or supervision by a licensed master rigger |  | Yes | Yes | Yes

## E104.2.1
TABLE E104.2.1
DWELLING OR SLEEPING UNITS WITH ACCESSIBLE COMMUNICATION FEATURES
TOTAL NUMBER OF DWELLING OR SLEEPING UNITS PROVIDED | MINIMUM REQUIRED NUMBER OF DWELLING OR SLEEPING UNITS WITH ACCESSIBLE COMMUNICATION FEATURES
1 | 1
2 to 25 | 2
26 to 50 | 4
51 to 75 | 7
76 to 100 | 9
101 to 150 | 12
151 to 200 | 14
201 to 300 | 17
301 to 400 | 20
401 to 500 | 22
501 to 1,000 | 5% of total
1,001 and over | 50 plus 3 for each 100 over 1,000

## E106.2
TABLE E106.2
WHEELCHAIR-ACCESSIBLE TELEPHONES
NUMBER OF TELEPHONES PROVIDED ON A FLOOR, LEVEL OR EXTERIOR SITE | MINIMUM REQUIRED NUMBER OF WHEELCHAIR-ACCESSIBLE TELEPHONES
1 or more single unit | 1 per floor, level and exterior site
1 bank | 1 per floor, level and exterior site
2 or more banks | 1 per bank

## 1-1
TABLE 1-1
FLOOD DESIGN CLASS OF BUILDINGS AND STRUCTURES
USE OF OCCUPANCY OF BUILDINGS AND STRUCTURES | FLOOD DESIGN CLASS
Buildings and structures that normally are unoccupied and pose minimal risk to the public or minimal disruption to the community should they be damaged or fail due to flooding. Flood Design Class 1 includes: 1. certain temporary structures that are in place for less than 180 days, 2. accessory storage buildings and minor storage facilities, 3. small structures used for parking of vehicles, and 4. certain agricultural structures.ᵃ | 1
Buildings and structures that pose a moderate risk to the public or moderate disruption to the community should they be damaged or fail due to flooding, except those listed as Flood Design Classes 1, 3, and 4. Flood Design Class 2 includes the vast majority of buildings and structures that are not specifically assigned another Flood Design Class, including most residential, commercial, and industrial buildings. | 2
Buildings and structures that pose a high risk to the public or significant disruption to the community should they be damaged, be unable to perform their intended functions after flooding, or fail due to flooding. Flood Design Class 3 includes: 1. buildings in which 300 or more persons may assemble in one place, such as theaters, lecture halls, and religious institutions with large areas used for worship; 2. museums; 3. community centers and other recreational facilities; 4. athletic facilities with seating for spectators; 5. elementary schools, secondary schools, and buildings with college or adult education classrooms; 6. jails, correctional facilities, and detention facilities; 7. healthcare facilities not having surgery or emergency treatment capabilities; 8. care facilities where residents have limited mobility or ability, including nursing homes but not including care facilities for five or fewer persons; 9. preschool and child care facilities not located in one- and two-family dwellings; 10. buildings and structures associated with power generating stations, water and sewage treatment plants, telecommunication facilities, and other utilities which, if their operations were interrupted by a flood, would cause significant disruption in day-to-day life or significant economic losses in a community; and 11. buildings and other structures not included in Flood Design Class 4 (including but not limited to facilities that manufacture, process, handle, store, use, or dispose of such substances as hazardous fuels, hazardous chemicals, hazardous waste, or explosives) containing toxic or explosive substances where the quantity of the material exceeds a threshold quantity established by the authority having jurisdiction and is sufficient to pose a threat to the public if released.ᵇ | 3
Buildings and structures that contain essential facilities and services necessary for emergency response and recovery, or that pose a substantial risk to the community at large in the event of failure, disruption of function, or damage by flooding. Flood Design Class 4 includes: 1. group I-2 occupancies having surgery or emergency treatment facilities; 2. fire, rescue, ambulance, and police stations and emergency vehicle garages; 3. designated emergency shelters; 4. designated emergency preparedness, communication, and operation centers and other facilities required for emergency response; 5. power generating stations and other public utility facilities required in emergencies; 6. structures containing highly toxic materials as defined by Section 307 where the quantity of the material exceeds the maximum allowable quantities of Table 307.1(2); 7. critical aviation facilities such as control towers, air traffic control centers, and hangars for aircraft used in emergency response; 8. ancillary structures such as communication towers, electrical substations, fuel or water storage tanks, or other structures necessary to allow continued functioning of a Flood Design Class 4 facility during and after an emergency; 9. buildings and other structures having critical national defense functions; and 10. water storage facilities and pump structures required to maintain water pressure for fire suppression. | 4

## 2-1
TABLE 2-1
MINIMUM ELEVATION OF THE TOP OF LOWEST FLOOR FLOOD HAZARD AREAS OTHER THAN COASTAL HIGH-HAZARD AREASᵃ, COASTAL A-ZONESᵃ
FLOOD DESIGN CLASSᵇ | MINIMUM ELEVATION, RELATIVE TO BASE FLOOD ELEVATION (BFE) OR DESIGN FLOOD ELEVATION (DFE)
1ᶜ | DFE = BFE + 2 ft
2ᵈ | DFE = BFE + 2 ft
3ᵈ | DFE = BFE + 2 ft
4ᵈ | DFE = BFE + 2 ft, or 500-year flood elevation, whichever is higher

## 4-1
TABLE 4-1
MINIMUM ELEVATION OF BOTTOM OF LOWEST SUPPORTING HORIZONTAL STRUCTURAL MEMBER OF LOWEST FLOOR COASTAL HIGH-HAZARD AREAS AND COASTAL A-ZONES
FLOOD DESIGN CLASSᵃ | MINIMUM ELEVATION, RELATIVE TO BASE FLOOD ELEVATION (BFE) OR DESIGN FLOOD ELEVATION (DFE)
1 | DFE = BFE + 2 ft
2 | DFE = BFE + 2 ft
3 | DFE = BFE + 2 ft
4 | DFE = BFE + 2 ft, or 500-year flood elevation, whichever is higher

## 5-1
TABLE 5-1
MINIMUM ELEVATION BELOW WHICH FLOOD-DAMAGE-RESISTANT MATERIALS SHALL BE USED
FLOOD DESIGN CLASSᵃ | MINIMUM ELEVATION IN FLOOD HAZARD AREAS, OTHER THAN COASTAL HIGH-HAZARD AREAS AND COASTAL A-ZONES, RELATIVE TO DESIGN FLOOD ELEVATION (DFE) | MINIMUM ELEVATION IN COASTAL HIGH-HAZARD AREAS AND COASTAL A-ZONES, RELATIVE TO DESIGN FLOOD ELEVATION (DFE)
1 | DFE = BFE + 2 ft | DFE = BFE + 2 ft
2 | DFE = BFE + 2 ft | DFE = BFE + 2 ft
3 | DFE = BFE + 2 ft | DFE = BFE + 3 ft
4 | DFE = BFE + 2 ft, or 500-year flood elevation, whichever is higher | DFE = BFE + 3 ft, or 500-year flood elevation, whichever is higher

## 6-1
TABLE 6-1
MINIMUM ELEVATION OF FLOODPROOFING FLOOD HAZARD AREAS OTHER THAN COASTAL HIGH-HAZARD AREASᵃ
FLOOD DESIGN CLASSᵇ | MINIMUM ELEVATION OF FLOODPROOFINGᶜ RELATIVE TO DESIGN FLOOD ELEVATION (DFE)
1 | DFE = BFE + 2 ft
2ᵈ | DFE = BFE + 2 ft
3 | DFE = BFE + 2 ft
4 | DFE = BFE + 2 ft, or 500-year flood elevation, whichever is higher

## 7-1
TABLE 7-1
MINIMUM ELEVATION OF ATTENDANT UTILITIES AND EQUIPMENT
FLOOD DESIGN CLASSᵃ | LOCATE ATTENDANT UTILITIES AND EQUIPMENT ABOVEᵇ
FLOOD DESIGN CLASSᵃ | MINIMUM ELEVATION IN FLOOD HAZARD AREAS, OTHER THAN COASTAL HIGH-HAZARD AREAS AND COASTAL A-ZONES, RELATIVE TO DESIGN FLOOD ELEVATION (DFE) | MINIMUM ELEVATION IN COASTAL HIGH-HAZARD AREAS AND COASTAL A-ZONES, RELATIVE TO DESIGN FLOOD ELEVATION (DFE)
1 | DFE = BFE + 2 ft | DFE = BFE + 2 ft
2 | DFE = BFE + 2 ft | DFE = BFE + 2 ft
3 | DFE = BFE + 2 ft | DFE = BFE + 3 ft
4 | DFE = BFE + 2 ft, or 500-year flood elevation, whichever is higher | DFE = BFE + 3 ft, or 500-year flood elevation, whichever is higher

## H112.6
TABLE H112.6
THICKNESS OF PROJECTING SIGNS
PROJECTION (feet) | MAXIMUM THICKNESS (feet)
5 | 2
4 | 2.5
3 | 3
2 | 3.5
1 | 4

## 8.5.5
TABLE 8.5.5
Component-Based Allowable Design Stresses
Component | Allowable Design Parameter
| Seismic Zones Criteria [Note(1)] | Building Code
|  | IBC, ASCE/SEI-7 | NBCC 2005 or Later
Structural, steel | 0.88Fy | 0.6Fy | 0.6Fy
Structural, other materials | Follow allowable limits as recommended by design specifications for material of use | Follow allowable limits as recommended by design specifications for material of use | Follow allowable limits as recommended by design specifications for material of use
Balustrades | < Fy | 0.6Fy | 0.6Fy
Structural glass in balustrades | Minimum factor of safety = 2 based on the modulus of rupture | Minimum factor of safety = 2 based on the modulus of rupture | Minimum factor of safety = 2 based on the modulus of rupture
Structural fastenings and/or connections | See 8.4.2.3.3 | Per 8.4.2.3 | Per 8.4.2.3

## N1
TABLE N1
REQUIRED INSPECTION AND TEST INTERVALS IN "MONTHS" (1)
Reference Code | Equipment Type (5) | Requirement | Interval | Periodic Inspections on Behalf of Owner By an Approved Agency (2) |  |  |  | Category Tests (3) on Behalf of Owner By an Approved Agency (4)
|  |  |  | Notifications | Filing | Approved agency (Inspecting) | Approved Agency (Witnessing) | Category 1 |  | Category 5 |  | Notifications | Filing | Approved agency (Performing) | Approved Agency (Witnessing)
[8 empty] | Requirement ent | Interval | Requirement ent | Interval
ASME A17.1 | Electric Elevators | 8.11.2.1 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19 | 1-1 to 12-31 | 8.6.4.20 | 60 | Yes (Cat. 5) | Yes | Yes | Yes
ASME A17.1 | Hydraulic Elevators | 8.11.3.1 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.5.14 | 1-1 to 12-31 | Roped 8.6.5.16 | 60 | Yes (Cat. 5) | Yes | Yes | Yes
ASME A17.1 | Escalators & Moving Walks | 8.11.4.1 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.8.15 | 1-1 to 12-31 | N/A | N/A | Yes (Cat. 1) | Yes | Yes | Yes
ASME A17.1 | Sidewalk Elevators | 8.11.5.1 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | Yes (Cat. 5) | Yes | Yes | Yes
ASME A17.1 | Dumbwaiters | 8.11.5.4 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | Material Lifts | 8.11.5.5 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | Special Purpose Personnel Elevators | 8.11.5.6 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | Inclined Elevators | 8.11.5.7 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | Shipboard Elevators | 8.11.5.8 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | Screw-Column Elevators | 8.11.5.9 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | Rooftop Elevators | 8.11.5.10 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | Rack and Pinion Elevators | 8.11.5.11 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | Limited Use-Limited Application Elevators (Commercial Bldgs. Only) | 8.11.5.12 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | Yes (Cat. 5) | Yes | Yes | Yes
ASME A17.1 | Elevators Used for Construction | 8.11.5.13 | 1-1 to 12-31 | No | Yes | Yes | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | Yes
ASME A18.1 | Platform/Stairway Chair Lifts | 10.2 | 1-1 to 12-31 | No | Yes | Yes | No | 10.3.1 | 1-1 to 12-31 | 10.3.3 | 60 | No | Yes | Yes | No
ASME B20.1 | Vertical and Inclined Reciprocating Conveyors (VRC) and Tow Conveyors | No | No | No | No | No | No | Appendix K2 | Appendix K2 | Appendix K2 | Appendix K2 | No | Yes | Yes | No
ASME A90.1 | Manlifts | 8.2 | 1-1 to 12-31 | No | Yes | Yes | Yes | 8.1 | 1-1 to 12-31 | N/A | N/A | No | Yes | Yes | Yes
ASME A17.1 | PR Elevators | No | No | No | No | No | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | Yes | Yes | No
ASME A17.1 | PR Dumb-waiters | No | No | No | No | No | No | 8.6.4.19, 8.6.5.14 | 1-1 to 12-31 | 8.6.4.20, 8.6.5.16 | 60 | No | No | No | No
ASME A18.1 | PR Platform/Stairway Chair Lifts | No | No | No | No | No | No | 10.3.1 | 1-1 to 12-31 | 10.3.3 | 60 | No | No | No | No

## 8.16.2.4.2
TABLE 8.16.2.4.2
SECTIONAL OR FLOOR VALVE SIZE
MINIMUM SIZE OF DRAIN CONNECTION
Up to 2 in. | 1 in.
2½ in. to 4 in | 1¼ in.
5 in. and larger | 2 in.

## U103.8
*TABLE U103.8
MINIMUM CLEAR WIDTH OF FIRE DEPARTMENT ACCESS PATH AND MAXIMUM NUMBER OF STORIES OF AN ADU
Width of fire department access path | ADU arrangementᵃ | Sprinklerᶜ | Fire district | Construction class | Maximum building height in stories | Fire separation distance
5 ft | Attachedᵇ, detached, manufactured home | SP | Outside | All | 2 | As permitted by Table 602
5 ft | Attachedᵇ, detached, manufactured home | SP | Inside | IA, IB, IIA, IIB, IIIA, IIIB, VA | 2 | As permitted by Table 602
5 ft | Attachedᵇ, detached, manufactured home | SP | Inside | VB | 1 | As permitted by Table 602
8 ft | Attachedᵇ, detached, manufactured home | SP | Inside | All | 2 | As permitted by Table 602